SECTION 2300

PLAIN AND REINFORCED CONCRETE

- SCOPE

- APPLICABLE STANDARDS

- SUBMITTALS

- MATERIALS

- DELIVERY, STORAGE AND HANDLING

- EXECUTION

- TEST OF CONCRETE QUALITY

- FINISHING OF FORMED SURFACES

- REPAIR OF SURFACE DEFECTS

- CONCRETE CONSTRUCTION TOLERANCES

- ACCEPTANCE OF STRUCTURE

- MEASUREMENT & PAYMENT

1.	SCOPE

The work under this section of the specification consists of furnishing all plant, labour, equipment, appliances and materials and in performing all operations in connection with the supply and installation of plain and reinforced concrete work complete in any floor and at any height as per drawings except where specifically stated in the relevant item of Bill of Quantities, in strict accordance with this section of the specifications and the applicable drawings, and subject to the terms and conditions of the Contract. The scope of this section of specification is covered with detailed specifications as laid down herein.

2.   	APPLICABLE STANDARDS

Latest editions of the following Pakistan, British and ASTM Standards are relevant to these specifications wherever applicable.

2.1	ASTM (AMERICAN SOCIETY FOR TESTING AND MATERIALS)

B     370   	Copper sheet and strip for building construction.

C       33   	Concrete Aggregates.

C       40   	Organic impurities in sand for concrete.

C       87   	Effect of organic impurities in fine aggregates on of mortar.

C       88   	Soundness of aggregates.

C       94  	Ready mixed Concrete.

C     109   	Compressive strength of hydraulic cement mortars.

C     117   	Material finer than No.200 (0.075mm) sieve.

C     123   	Light-weight pieces in aggregates.

C     125   	Concrete and concrete aggregates.

C     127   	Specific gravity and absorption of coarse aggregate.

C     128   	Specific gravity and absorption of fine aggregate.

C     131   	Resistance to abrasion of small size coarse aggregates.

C     136   	Sieve or screen analysis of fine and coarse aggregate.

C     142   	Clay lumps and friable particles in aggregates.

C     143   	Slump of Portland Cement Concrete.

C     144   	Aggregate for masonry mortar.

C     150   	Portland Cement.

C     156   	Water retention by concrete curing material

C     171   	Sheet material for curing concrete.

C     185   	Air content or hydraulic cement mortar.

C     188   	Density of hydraulic cement.

C     191   	Time of setting of hydraulic cement by vicat needle.

C     260   	Air entraining admixtures for concrete.

C     289   	Potential reactivity of aggregate.

C     309   	Liquid membrane-forming compounds for curing concrete.

C     330   	Lightweight aggregates for structural concrete.

C     331   	Lightweight aggregates for concrete masonry.

C     332   	Lightweight aggregates for insulating concrete.

C     494   	Chemical admixtures for concrete.

C     535   	Resistance to abrasion of large size coarse aggregates.

C     567   	Unit weight of structural lightweight concrete.

D       75   	Aggregate sampling.

D     994   	Preformed expansion joint filler for concrete.

D   1190   	Concrete joint sealer (hot poured elastic type).

D   1751   	Preformed expansion joint filler for concrete paving and structural construction.

D   1752   	Preformed sponge rubber and cork expansion joint fillers for concrete paving and structural construction.

D   1850   	Concrete joint sealer (cold application type).

E       11   	Wire cloth sleeves for testing purposes.

E       96   	Water vapor transmission of materials in sheet form.

E     154   	Materials for use as vapor barrier under concrete slabs.

E     337   	Relative humidity by wet and dry bulb psychrometer.

2.2	ACI (AMERICAN CONCRETE INSTITUTE)

211.1 	Recommended practice for selecting proportions for normal and heavy weight concrete.

214  	Recommended practice for evaluation of strength test result of concrete

301   	Specifications for structural concrete for buildings.

304   	Recommended practice for measuring, mixing, transporting and placing concrete.

305   	Hot weather concreting.

306.1-90 Standard Specifications for Cold Weather Concreting

306R-88 Cold Weather Concreting

308   	Recommended practice for curing concrete.

309 	Recommended practice for consolidation of concrete.

318   	Building code requirements for reinforced concrete.

347   	Recommended practice for concrete formwork.

512   	Pre-cast structural concrete in building.

517   	Low pressure steam curing.

533   	Fabrication, handling and erection of pre-cast concrete wall panels.

2.3	BRITISH STANDARDS

BS       12   	Portland cement, ordinary and rapid hardening.

BS     410   	Test Sieves.

BS     812   	Methods for the sampling and testing of mineral aggregates, sands and fillers.

BS     882   	Coarse and fine aggregates from natural sources.

BS   1305   	Batch Mixer.

BS   1881   	Methods of testing and sampling concrete.

BS   3148   	Tests for water for making concrete.

BS   3837   	Expanded polystyrene boards.

BS   5328   	Structural Concrete.,

BS   3869   	Rigid expanded polyvinyl chloride for thermal insulation.

BS   3927	Phenolic foam materials for thermal insulation and building applications.

BS   4027   	Sulphate-resisting Portland cement.

BS   8110   	Structural use of concrete.

CP     114   	Structural use of reinforced concrete in buildings.

CP     116   	Structural use of precast concrete.

CP   5337   	The structural use of concrete for retaining aqueous liquids.

In addition, the latest editions of other Pakistan and British Standards, American Concrete Institute Standards, American Society for Testing and Materials Standards and other Standards as may be specified by the Engineer for special Materials and Construction are also relevant.

3.	SUBMITTALS

3.1	Suitable templates or instructions or both shall be provided for setting out items not placed in the forms. Embedded items and other materials for mechanical and electrical operations shall have been completed, inspected, tested and approved before concrete is placed.

3.2	For special concrete finish and for special methods of construction (e.g. slip forms) formwork shop drawings shall be designed and prepared by the Contractor, at his own cost. Approval of shop drawings as well as that of actual samples of concrete finish shall be obtained before work is commenced.

3.3	The Contractor shall supply to the Engineer at fortnightly intervals, test certificates with the appropriate standard in respect of the samples of cement from the work-site.

These tests shall be carried out in a laboratory approved by the Engineer.

3.4	The grading of the coarse and fine aggregates shall be tested at least once for every 100 tons supplied, to ensure that the grading is uniform and same as that of the samples used in the preliminary tests.

3.5	Where doubt exists as to the suitability of the water, it shall be tested in accordance with BS 3148.

3.6	The Contractor shall provide Mix design by weight for each class of concrete.

Manufacture 12 test cubes for each 3 mix design batches (6 x 6 x 6) inches in accordance with the Mix design batching by weight and test 3 cubes each at 3,7,14 & 28 days intervals in the presence of Engineer's Representative and submit all relevant data and results of tests for approval of the Engineer.  The Contractor shall obtain approval from the Engineer in writing for each Mix design before producing the actual concrete for the Works.

3.7	'Workability' of Concrete shall be determined by either the slump or compaction factor tests as directed by the Engineer and these shall be performed in accordance with the methods given ASTM C 143.

The slump or compaction factor for each class of concrete shall be determined during the preliminary Test mixes and the value obtained shall not be modified without the written consent of the Engineer.

3.8	Manufacturer's recommendations and instructions along with the sample of material shall be submitted to the Engineer for his approval.

3.9	The Contractor shall, at his own cost, make optimum mix design and testing for approval of the composition of Non Shrinking grout and Non Shrink second stage Concrete Grout, prior to Commencement of the work.

3.10	The Contractor shall be required to submit a sample of pre-cast unit for the approval of the Engineer; all pre-cast units shall strictly conform to the approved sample. The proposal for transporting and erecting pre-cast units in position shall also be submitted by the Contractor for the approval of the Engineer.

4.   	MATERIALS

4.1     	Aggregates

4.1.1	The sources of supply of all fine and coarse aggregates shall be subject to the approval of the Engineer.

4.1.2 	All fine and coarse aggregates shall be clean and free from clay, loam, silt and other deleterious matter.  If required, the Engineer reserves the right to have them washed by the Contractor at no additional expense.  Coarse and fine aggregates shall be delivered and stored separately at site.  Aggregates shall not be stored on muddy ground or where they are likely to become dirty or contaminated.

4.1.3	Fine aggregate shall be hard coarse sand, crushed stone or gravel screenings and shall conform to requirements of PS 243 and/or BS 882 and/or ASTM C 33.  Only fine aggregate of grading zones 1 to 3 (BS 882) shall be used.

4.1.4	Coarse aggregate shall be gravel or crush stone of hard, durable material free from laminated structure and conforming to PS 243 and/or BS 882 and/or ASTM C 33 graded as follows for use in mass concrete as in foundations:

# Total Passing B.S. Sieve          		Percent by weight

3 in.    		(76.20 mm)           :        		  100

1.5 in.  		(38.10 mm)           :         		95-100

0.75 in. 	             (19.05 mm)        	   :         		 30-70

0.38 in. 		(9.52 mm)             :         		 10-35

0.19 in. 		(4.76 mm)             :          	  0-5

Coarse aggregate for all cast-in-place concrete other than mass concrete as for foundations shall be graded with the following limits:

# Total Passing B.S. Sieve          		Percent by weight

1.5 in.  		(38.10 mm)           :         		 100

0.75 in. 	(19.05 mm)           :          	95-100

0.38 in.  	(9.52 mm)             :		25-55

0.19 in   	(4.76 mm)             :           	 0-10

4.1.5	Wherever feasible, the nominal maximum size of aggregate for cast- in- place reinforced concrete slabs and other members shall be 3/4 inch. If there are difficulties in placing such concrete the maximum size may be restricted to 1/2 inch provided the requirements for strength are satisfied. The grading requirements of 1/2 inch or 3/8 inch down aggregate shall be agreed to with the Engineer as per relevant ASTM/BS standards.

4.1.6	The nominal maximum size of the aggregate for precast concrete shall not be larger than one fifth of the narrowest dimension between sides of forms, or one-third of the depth of slabs or three-fourths of the minimum clear distance between reinforcing bars or between bars and forms, whichever is least.  In Precast columns the nominal maximum size of the aggregate shall be limited as above but shall not be larger than two-thirds of the minimum clear distance between bars.

4.1.7	Coarse aggregates in precast concrete of normal weight may be of one maximum size for all concrete placed in 1 day when quantities to be placed are too small to permit economical use of more than one mix design.

When a single mix design is so used, the maximum nominal size shall be as required for the most critical condition of concreting, in accordance with the requirements of clause (4.1.6) above.

4.1.8	Except were it can be shown to the satisfaction of the Engineer that a supply of properly graded aggregate of uniform quality can be maintained over the period of the work, the grading of the aggregates shall be controlled by obtaining the 19.05 mm maximum nominal size, the different size being stocked in separate stock piles and recombined in the correct proportion for each batch at the batching plant. The materials shall be stock-piled for a period before use so as to drain nearly to constant moisture content (as long as site and other conditions permit, preferably for atleast a day). The grading of the course and fine aggregates shall be tested atleast once for every 100 tons supplied to ensure that the grading is uniform and the same as that of the samples used in the preliminary tests.

4.1.9	For use in fireproof concrete, the aggregates shall be fire clay and semi-acidic fine ground.  The use of broken fire clay bricks as coarse aggregate and waste of semi-acidic refractory particles as fine aggregate can be allowed.

4.2	CEMENT

4.2.1	The cement shall be fresh and of approved origin and manufacture.  It shall be one of the following as may be specified by the Engineer.

-   	Ordinary or Rapid Hardening Portland cements complying with the requirements of PS 232 or BS 12 or ASTM C 150.

-   	Sulphate Resisting Portland/Cement complying with the requirements of PS 612 or BS 4027 or ASTM C 150.

4.2.2	Unless otherwise specified, ordinary Portland cement complying with the requirements of BS 12 shall be used.

4.2.3	For all fair faced concrete it will be necessary to use approved cement with a view to obtain light shade concrete as approved by the Engineer.

4.2.4	Only one brand of each type of cement shall be used for concrete in any individual member of the structure.  Cement shall be used in the sequence of receipt of shipment, unless otherwise directed.

4.2.5 	There shall be sufficient cement at site to ensure that each section of work is completed without interruption.

4.2.6	Cement reclaimed from cleaning of bags or from leaky containers shall not be used.

4.2.7	The Contractor shall provide and erect (at his own cost) in a suitable plane, dry, well ventilated, weather-proof and water proof shed of sufficient capacity to store the cement.

4.2.8	Cement shall be used as soon as possible after delivery and cement which the Engineer considers has become stale or unsuitable through absorption of moisture from the atmosphere or otherwise shall be rejected and removed immediately from the site at the Contractor's expense.  Any cement in containers damaged so as to allow the contents to spill or permitting access of the atmosphere prior to opening of the container at the time of concrete mixing shall be rejected and removed immediately from the site at the Contractor's expense.

4.2.9	The mixing together of different types of cement will not be permitted.

4.3	WATER

Only clean water from the city supply, tube well installed at the site or from other sources approved by the Engineer shall be used.  The Contractor shall supply sufficient water for all purposes, including mixing the concrete, curing and cleaning plant and tools.  Where water can be shown to contain any sugar or an excess of acid, alkali or salt, the Engineer may refuse to permit its use.

In case of doubt, the Engineer may require that concrete mixed with water proposed to be used should not have a compressive strength lower than 90 percent of the strength of concrete mixed with distilled water.

  - ADMIXTURES

    - General

Admixtures shall be furnished by the contractor and used only with the written permission of the Engineer. If air entraining agents, water reducing agents , set retarders or strength accelerators are permitted to be used they shall not be used in greater dosages than those recommended by the manufacturer, or permitted by the engineer, and shall conform to the requirements for each of the agents specicified by the manufacturer. Admixtures shall be well agitated to ensure uniformity before use in concrete. The contractor may use a retarder to facilitate preparation of construction joints, subject to the approval of Engineer as to the composition of retarder and its time of application.

    - Specifications

Air entraining admixtures shall comply with ASTM Designation C-260.All other admixtures shall comply their relevant section of ASTM Designation C-494 Typed. Admixtures shall not contain calcium chloride. Approval shall be given on certification of conformance provided by an independent laboratory, and after checking their performance in trial mixes. Admixtures shall be well subject to sampling and testing. Admixture shall be handled and stored in accordance with the manufacturer’s recommendations.

    - Removal of Unsatisfactory Material

If tests prove that any admixture, which has been delivered, is unsatisfactory, it shall be promptly removed from the site.

    - Batching

Each Admixture shall be accurately batched by mechanical batcher and shall be added in a manner which ensures uniform distribution throughout the batch.

    - Compatibility

The compatibility of different admixtures used in the same batch shall be established to the satisfaction of the engineer.

    - Air Entraining Agent

Field Tests on air-entrained mixes shall be made in accordance with ASTM Designation C-231.Concrete produced with air contents exceeding the specified limits shall be rejected by the engineer.

    - Storage

Admixtures shall be stored in suitable containers, which will maintain them in uniform solution and will protect them from weather and contamination.

    - Storage Time

Admixtures, which have been in storage for more than 6 months, shall not be used unless retest proves tem to be satisfactory. Costs of all such retests shall be borne by the Contractor. Rejected materials shall be removed immediately from the site.

    - Measurement

Measurements of admixtures for acceptably completed works shall be made separately on the basis of litres of each admixture used during concreting.

All additives such as foaming and water proofing agents shall be from a manufacturer approved by the Engineer.

4.5   	NOMINAL CONCRETE MIXES

4.5.1   Proportions of Mix

a)	Cement and aggregates:

Cement, fine aggregate and the coarse aggregate shall be weighed separately.  The proportions of cement to fine aggregate and coarse aggregate shall be adjusted so as to provide the concrete of the required crushing strength when tested as set out in Table 1.

b)	The Contractor shall regulate and arrange mixing of the ingredients for the designed mix of the concrete by weight batching.  The cost of designing the mix shall be borne by the Contractor.

c)	Water/Cement ratio:

The quantity of water used shall be just sufficient to produce dense concrete of adequate strength and workability for its purpose.  For all concrete, water/cement ratio shall not exceed 0.45, except that for water retaining structures water/cement ratio shall not exceed 0.40.

d)	Workability:

The workability shall be controlled by direct measurement of the water content, allowance being made for any water in the fine and coarse aggregates.  The concrete shall be just sufficiently workable to be placed and compacted, without difficulty, by the available means.

Unless otherwise permitted or specified, the concrete shall be proportioned and produced to have a slump of 3 inch or less for consolidation by vibration. A tolerance of upto 1 inch above the indicated maximum shall be allowed for individual batches provided the average for all batches or the most recent 10 batches tested, which ever is fewer, does not exceed the maximum limit.  Concrete of lower than usual slump may be used provided it is properly placed and consolidated.

4.5.2	Strength requirements for concrete

a)	Concrete made with Portland cement shall comply with the cube strength requirements of Table 1, columns 5 & 6 (Works Test). Cylindrical Compressive Strength shall comply with ACI 214.

Table 1: Cube Strength requirements for Portland concrete with aggregates complying with BS. 882.

| Class of Concrete | Min Cement per Cu.ft of compacted concrete (lb.) | Cube strength at 28 days after mixing & pouring (psi) | Alternative Cube strength at 7 days after mixing & pouring (psi) |
| --- | --- | --- | --- |

|  |  | Preliminary | Work | Preliminary | Work |
| --- | --- | --- | --- | --- | --- |
|  |  | Tests | tests | tests | tests |
| 1 | 2 | 3 | 4 | 5 | 6 |
| A1 | 30.00 | 7700 | 5725 | 5150 | 3800 |
| A2 | 30.00 | 9000 | 6725 | 6050 | 4500 |
| A | 30.00 | 6300 | 4725 | 4250 | 3200 |
| B | 22.00 | 5000 | 3750 | 3300 | 2500 |
| C | 18.00 | 4000 | 3000 | 2700 | 2000 |
| D | 13.00 | 2000 | 1500 | 1350 | 1000 |
| E | 9.50 | ------ | 1000 | ------ |  |

Note: 	Conversion Factors. 	1 psi = 0.006894 MPa  	1 gal   = 4.54 liter

1 lb.  = 0.4537 Kg.  										1cu.ft. = 0.028 cum.

b)	The strengths given in Table 1 are based on the assumption that average temperature is 20 degree C. Where accurate records of temperature are kept, allowance may be made for change of temperature or the cubes may be tested at the equivalent maturity.

c)	All structural concrete shall conform to BS 5328 or ACI 301M.

4.6    	PVC WATER STOP/HYDROFOIL

All PVC water stops/hydrofoil shall be central bulb type from a manufacturer approved by the 'Engineer'.  The specific gravity of PVC water stop/hydrofoil shall not be less than 1.37 and full stretch Break cut intensity when tested at normal temperature shall not be less than 1875 psi.

The material shall have a modulus of rigidity of 850 psi at +10o C and 10,500 psi. at 20o C.

5.	DELIVERY, STORAGE AND HANDLING

5.1	Except where it can be shown to the satisfaction of the Engineer that a supply of properly graded aggregate of uniform quality can be maintained over the period of the work, the grading of the aggregates shall be controlled by obtaining the 3/4" maximum nominal size, the different sizes being stocked in separate stock piles and recombined in the correct proportion for each batch at the batching plant.  The materials shall be stockpiled for a period before use so as to drain nearly to constant moisture content (as long as site and other conditions permit, preferably for at least a day).

5.2	The Contractor shall provide and erect (at his cost) a suitable plain, dry, well ventilated, weatherproof and water proof shed of sufficient capacity to store the cement.

6.	EXECUTION

  - CAST-IN-SITU CONCRETE WORK

6.1.1	Batching

a) 	All cement, including cement supplied in bulk, shall be batched by weight.  A bag of cement may be taken as weighing 110 lb. with the prior approval of the Engineer.

b)	Aggregates shall be batched by weight, due allowance being made for water content.  Aggregates may be batched by volume through conversion of weigh batching, only with the prior permission of the Engineer. The apparatus for weight batching may be an integral part of the mixer or a separate unit of a type approved by the Engineer.  It shall be accurate within 2% and shall be checked for accuracy at least once a week.

c)	The quantity of additives i.e. foaming and water proofing agents etc. shall be as prescribed by the manufacturer or as directed by the Engineer.

d)	Where the batching plant is of the type in which cement and aggregates are weighed in the same compartment, the cement shall be introduced into the compartment between two sizes of aggregates.

e)	Each batch shall be so charged into the mixer that some water will enter in advance of the cement and aggregates.  Water shall continue to flow for a period, which may extend to the end of the first 25 percent of the specified mixing time. Controls shall be provided to prevent batched ingredients from entering the mixer before the previous batch has been completely discharged.

6.1.2   	Mixing

a)	The concrete shall be mixed in an approved batch mixer conforming to the requirements of BS 1305 or ACI 304R (ASTM C685). It shall be fitted with the manufacturer's plate stating the rates, capacity and the recommended number of revolutions per minute and shall be operated in accordance therewith. It shall be equipped with a suitable charging mechanism and an accurate water-measuring device. The mixer shall be capable of thoroughly combining the aggregates, cement and water into a uniform mass within the specified mixing time and of discharging the concrete without harmful segregation.

b)	Mixing shall continue for the period recommended by the mixer manufacturer or until there is apparently a uniform distribution of the materials and the mass is uniform in colour, whichever period is longer.  If it is desired to use a mixing period of less than 1-1/2 minutes, the Engineer's approval shall be obtained in writing.

c)	Controls shall be provided to ensure that the batch cannot be discharged until the required mixing time has elapsed.  At least three quarters of the required mixing time shall take place after the last of the mixing water has been added.

d)	The interior of the mixer shall be free of accumulations that will interfere with mixing action.  Mixing blades shall be replaced when they have lost 10 percent of their original height.

e)	Concrete shall be mixed only in quantities for immediate use. Concrete which has set shall not be retempered, but shall be discarded.

6.1.3	Transporting

a)	The concrete shall be transported from the place of mixing to the place of final deposit as rapidly as practicable by means, which will prevent segregation or loss of ingredients. All skip vehicles, or containers used for transporting the concrete shall be thoroughly cleaned.

b)	During hot or cold weather, concrete shall be transported in deep containers, on account of their lower ratios of surface area to mass, which reduces the rate of loss of water, by evaporation during hot weather and loss of heat during cold weather.

6.1.4	Placing

The Contractor shall note that placing of concrete will be done with concrete pump as mentioned in Appendix-G to Tender, Volume-I of Tender Documents. No other method of placing of concrete will be allowed.

a)	Before placing of concrete, formwork shall have been completed; water shall have been removed; reinforcement shall have been secured in place; expansion joint material, anchors and other embedded items shall have been kept in position; and the entire preparation shall have been approved by the Engineer.

No concrete is to be placed into the foundation trenches until the ground to receive the same has been examined and approved by the Engineer for this purpose.

b)	The actual sequence of construction proposed by the Contractor shall be subject to the Engineer's approval before construction starts on any part of the structure, and this sequence shall not be varied without the Engineer's approval.

c)	The concrete after it has been mixed shall be placed as soon as it is practicable.  Once the concrete has left the mixer, no more water shall be added, although the concrete may be mixed or agitated to help maintain workability.  The concrete shall not be used if, through any cause, the workability of the mix at the time of placing is too low for it to be compacted fully and to an acceptable finish by whatever means available.

The time between mixing and placing should be reduced, if the mix is richer or the initial workability of the mix is lower than normal, or if a rapid hardening cement or an accelerator is used, or if the work is carried out at a high temperature or exposed to a drying atmosphere.

The Contractor shall ensure that the delay between mixing and placing including consolidation does not exceed 45 minutes under any circumstances.  Any concrete which does not satisfy this requirement shall be rejected.

d)	Concrete shall be deposited as nearly as possible in its final position to avoid segregation due to rehandling or flowing. In no circumstances may concrete be railed or made to flow along the forms by the use of vibrators.

e)	The free fall of concrete shall not be allowed to exceed 6 feet. Where it is necessary for the concrete to be lowered more than this depth, it is not to be dropped into its final position, but shall be placed through pipes fed by a hopper. When a pipe is used for placing concrete the lower end shall be kept inside or close to the freshly deposited concrete.  The size of the pipe shall be not less than 9 inch in diameter.

f)	The workmen carrying concrete to the site, and all other workmen moving about on the reinforcement before the concrete is placed, shall move only along runways or planks placed for the purpose and no person shall be allowed to walk on the reinforcement itself.

g)	Prior to the laying of concrete on load bearing masonry walls, bearing plates and at other points, as may be directed by the Engineer, the surface will be brought to a true, hard and smooth level surface using cement sand mortar in the ratio of 1 volume of cement to 3 volumes of sand.  Two layers of building paper weighing .082 lb./ft2 will then be laid flat to separate the concrete from the surface on which it is to be laid.

h)	Concrete shall be deposited continuously, or in layers of such thickness that no concrete will be deposited on concrete, which has hardened sufficiently to cause the formation of seams or planes of weakness within the section.  If a section cannot be placed continuously, construction joints shall be located as shown in the Contract Documents or as approved by the Engineer.  Placing shall be carried out at such a rate that the concrete which is being integrated with fresh concrete is still plastic.  Concrete which has partially hardened shall not be deposited.  Temporary spreaders in forms shall be removed when the concrete placing has reached an elevation rendering their services unnecessary. They may remain embedded in the concrete only if made of metal or concrete and if prior approval has been obtained.

i)	Every Contractor whose work is related to the concrete or services or must be supported by it shall be given ample notice and opportunity to introduce and/or furnish embedded items before the concrete is placed.

6.1.5	Construction Joints

a)	Construction Joints not shown on the drawings shall be so made and located as to least impair the strength of the structure and shall need prior approval of the Engineer.  In general, they shall be located near the middle of the spans of slabs and beams unless a secondary beam intersects a main beam at this point, in which case the joint in the main beam shall be offset a distance equal to twice the width of the secondary beam.  Joints in walls and columns shall be at the underside of floors, slabs or beams and at the top of footings or floor slabs. Beams, brackets, columns capitals, haunches and drop panels shall be placed at the same time as slabs. Joints shall be perpendicular to the main reinforcement.

b)	All reinforcing steel shall be continued across joints.  Keys and inclined dowels shall be provided as directed by the Engineer.  Longitudinal keys at least 1-1/2 inches deep shall be provided in all joints in walls and between walls and slabs or footings.

c)	When the work has to be resumed on a surface which has hardened, such surface shall be roughened in an approved manner which will expose the aggregate uniformly and will not leave laitance, loosened particles of aggregate or damaged concrete at the surface.

d)	The hardened concrete of construction joints and of joints between footings and walls or columns, between walls or columns and beams or floors they support, joints in un-exposed walls and all others not mentioned herein shall be dampened (but not saturated) immediately prior to placing of fresh concrete.

e)	The hardened concrete of joints in exposed work, joints in the middle of beams, and slabs; and joints in work designed to contain liquids shall be dampened (but not saturated) and then thoroughly covered with a coat of cement grout similar in proportions to the mortar in the concrete. The grout shall be as thick as possible on vertical surfaces and at least 1/2 inch thick on horizontal surfaces. The fresh concrete shall be placed before the grout has attained initial set.

f)	Where the concrete has not fully hardened, all laitance shall be removed by scrubbing the wet surface with wire or bristle, and brushed, care being taken to avoid dislodgment of particles of aggregate.  The surface shall then be coated with neat cement grout.  The first layer of concrete to be placed on this surface shall not exceed 6 inch in thickness, and shall be well rammed against old work, particular attention being paid to corners and closed spots.

g)	Stop ends for movement joints or construction joints shall be made by splitting them along the lines of reinforcement passing through them, so that each portion can be positioned and removed separately without disturbance or shock to the reinforcement or the concrete. Stop ends made of expanded metal or similar material may only be left permanently in the concrete with prior written approval of the Engineer.  Where such stop ends are used, no metal may be left permanently in the concrete closer to the surface of the concrete than the specified cover to the reinforcement.

6.1.6	Expansion Joints

Expansion joints shall be provided wherever indicated on the Drawings or as directed by the Engineer.  In no case shall the reinforcement, corner protection angles, or other embedded items be permitted to extend continuously through any expansion joint.

All expansion joints shall be carefully placed so as not to be displaced during concreting. The method of placing the expansion joints shall be strictly in accordance with the Drawings and/or as directed by the Engineer.

6.1.7	Placing and Connection of Water-Stops

The water-stops and expansion joint material shall be positioned accurately and supported against displacement as shown on the drawings.

6.1.8	Embedded Items

a)	Electric conduits and other pipes which are planned to be embedded shall not, with their fittings, displace more than four percent of the area of the cross section of a column on which stress is calculated or which is required for fire protection. Sleeves, conduits, or other pipes passing through floors, walls, or beams shall be of such size or in such location as not to impair unduly the strength of the construction; such sleeves, conduits, or pipes may be considered as replacing structurally in compression the displaced concrete, provided that they are not exposed to rusting or other deterioration, are of uncoated or galvanized iron or steel not thinner than standard steel pipe, have a nominal inside diameter not over 2 inch and are spaced not less than three diameters on centers. Except when plans of conduits and pipes are approved by the Engineer, embedded pipes and conduits other than those merely passing through, shall not be larger in outside diameter than one third the thickness of the slab, wall, or beams in which they are embedded nor so located as to impair unduly the strength of the construction.  Sleeve pipes, or conduits of any material not harmful to concrete and within the limitations of this section may be embedded in concrete with the approval of the Engineer provided they are not considered to replace the displaced concrete.

b)	All sleeves, inserts, anchors, and embedded items required for adjoining work or for its support shall be placed prior to concreting. Voids in sleeves, inserts and anchor slots shall be filled temporarily with readily removable material to prevent the entry of concrete into the voids.

6.1.10	Consolidation

a)	All concrete shall be consolidated by vibration, spading, rodding or forking so that the concrete is thoroughly worked around the reinforcement, around embedded items and into corners of forms, eliminating all air or stone pockets which may cause honeycombing, pitting, or planes of weakness.  Internal vibrators shall have a minimum frequency of 8000 vibrations per minute and sufficient amplitude to consolidate the concrete effectively. They shall be operated by competent workmen.  Use of vibrators to transport within forms shall not be allowed. Vibrators shall be inserted and withdrawn at points approximately 18 inch apart.  At each insertion, the duration shall be sufficient to consolidate the concrete but not excessive so as to cause segregation, generally from 5 to 15 sec.  A spare Vibrator shall be kept on the job site during all concrete placing operations.

Where the concrete is to have an as-cast finish, a full surface of mortar shall be brought against the form by the vibration process, supplemented, if necessary, by spading to work the coarse aggregate back from the formed surface.

b)	If there is any tendency for the mix to segregate during consolidation, particularly if this produces excessive laitance, the mix proportions shall be modified to effect an improvement in the quality of the concrete to the satisfaction of the Engineer and in conformity with the provisions of Clause 5.

c)	Vibrator shall not be allowed to contact the formwork for exposed concrete surfaces.

d)	Mechanical vibrators shall be of a type suited in the opinion of the Engineer to the particular conditions.

e)	Over-vibration or vibration of very wet mixes is harmful and should be avoided.

6.1.11	Curing and Protection

a)	Beginning immediately after placement, concrete shall be protected from premature drying, excessively hot or cold temperatures and mechanical injury and shall be maintained with minimum moisture loss at a relative constant temperature for the period necessary for hydration of the cement and hardening of the concrete. The materials and methods of curing shall be subject to approval of the Engineer.

b)	For concrete surfaces not in contact with forms, one of the following procedures shall be applied immediately after completion of placement and finishing:

-   	Ponding or continuous sprinkling.

-   	Application of absorptive mats or fabric kept continuously wet.

-   	Application of waterproof sheet materials approved by the Engineer.

-   	Application of other moisture-retaining covering as approved.

- Application of a curing compound conforming to ASTM C 309.

The compound shall be applied in accordance with the recommendations of the manufacturer immediately after any water sheen, which may develop after finishing has disappeared from the concrete surface.  It shall not be used on any surface against which additional concrete or other material is to be bonded unless it is proved that the curing compound will not prevent bond, or unless positive measures are taken to remove it completely from areas to receive bonded applications.

c)	Moisture loss from surfaces placed against wooden forms or metal forms exposed to heating by the sun shall be minimized by keeping the forms wet until they can be safely removed.  After form removal the concrete shall be cured until the end of the time prescribed for curing.

d)	Curing in accordance with sub-clause ‘a’ & ‘b’ above shall be continued for at least 10 days in the case of all concrete except concrete with rapid-hardening Portland Cement for which the period shall be at least 3 days.  Alternatively, if tests are made of cubes kept adjacent to the structure and cured by the same methods, moisture retention measures may be terminated when the average compressive strength has reached 70 percent of the minimum specified works cube strength.  If one of the first four curing procedures of sub-clause ‘b’ is used initially, it may be replaced by one of the other procedures of that sub-clause any time after the concrete is one day old provided the concrete is not permitted to become surface dry during the transition.

e)	When the mean daily outdoor temperature is less than 5 degree C (41 deg. F) temperature of the concrete shall be maintained between 10 and 20 degrees C (50 to 68 deg. F) for the required curing period of sub-clause‘d’.

When necessary, arrangements for heating, covering insulation or housing the concrete work shall be made in advance of placement and shall be adequate to maintain the required temperature without injury due to concentration of heat.  Combustion heaters shall not be used during the first 24 hours unless precautions are taken to prevent exposure of the concrete to exhaust gasses, which contain carbon dioxide.

f)	During hot weather when necessary, provision for wind-brakes, shading for spraying, sprinkling, ponding or wet covering with a light coloured material shall be made in advance of placement. Such protective measures shall be taken as quickly as concrete hardening and finishing operation will allow.

g)	Changes in temperature of the air immediately adjacent to the concrete during and immediately following the curing period shall be kept as uniform as possible and shall not exceed 3 deg. C (37 deg. F) in  any one hour or 10 degree C (50 deg. F )in any 24 hour period.

h)	During the curing period, the concrete shall be protected from damaging mechanical disturbances, such as load stresses, heavy shock and excessive vibrations.  All finished concrete surfaces shall be protected from damage by construction equipment, materials or methods by application of curing procedures, and by rain or running water. Self-supporting structures shall not be loaded in such a way as to over stress the concrete.

6.2  	WORKS IN EXTREME WEATHER

6.2.1	Unless adequate protection is provided and approval is obtained from the Engineer, concrete shall not be placed during rain.

Rainwater shall not be allowed to increase the mixing water nor to damage the surface finish.

6.2.2	When the temperature of the surrounding air is expected to be below 5 deg. C during placing or within 24 hours thereafter, the temperature of the plastic concrete, as placed, shall be no lower than 13 deg. C for sections less than 12 inch in any dimension nor 10 deg. C for any other sections.

When necessary, concrete material should be heated before mixing and carefully protected after placing, in general, heating or mixing water alone to about 60 deg. C may be sufficient for this purpose. Dependence should not be placed on salt or other chemicals for the prevention of freezing. No frozen material or materials, containing ice shall be used.  All concrete damaged by frost shall be removed.  It is recommended that concrete exposed to the action of freezing weather should have entrained air and the water content of the mix should not exceed 5.5 gallon/bag of cement.

If water or aggregate is heated above 38 deg. C the water shall be combined with the aggregate in the mixer before cement is added.  Cement shall not be mixed with water or with mixtures of water & aggregate having a temperature greater than 38 deg. C.

6.2..3	During hot weather, the temperature of the concrete as placed shall not be so high as to cause difficulty from loss of slump, flash set, or cold joints and should not exceed 32 deg. C. For massive concrete, this temperature should not exceed 21 degree C. When the temperature of the concrete exceeds 32 degree C, precautionary measures approved by the Engineer shall be put into effect.  When the temperature of the steel is greater than 50 deg. C, steel forms and reinforcement shall be sprayed with water just prior to placing the concrete.  The ingredients shall be cooled before mixing, or flaked ice or well crushed ice of a size that will melt completely during mixing may be substituted for all part of the mixing water if, due to high temperature, low slump, flash set or cold joints are encountered.

Other precautions recommended by ACI Standard 305-72 shall also be adopted.

7.     	TEST OF CONCRETE QUALITY

7.1   	The Contractor shall provide samples of concrete for testing at the Engineer's direction.  Proper facilities shall be provided for making and curing the test specimens.  A competent person shall be employed by the Contractor whose first duty shall be to supervise all stages in the preparation and placing of the concrete.  All test specimens shall be made and site tests carried out under his direct supervision.

7.2	Preliminary cube tests and works cube test shall be performed in accordance with the discretion of the Engineer. The standard of acceptance for preliminary and works tests shall be as given below.

7.3	The usual test for concrete with maximum size of aggregate upto 1-1/2 inch is the 6 inch cube tested in compression.  Details of the testing are given in Part 8 of BS 1881.

7.4	For all grades of concrete, preliminary cube strength test with the mixes and materials to be used shall be performed in accordance with BS 1881 before the work is begun and subsequently whenever any change is to be made in the materials or in the proportions of materials to be used, or as required by the Engineer. The strengths shall comply with the standard of quality specified in accordance with Table 1 for preliminary tests.  The cost of such testing shall be borne by the Contractor.

7.5	Test sample shall be taken at the mixer or as directed by the Engineer. The test specimens shall be cured in accordance with BS 1881.

Records shall be kept of all test cubes identifying the mix used the section of work for which the concrete was used and the date poured.

7.6	Five test cubes are to be tested for compressive strength as specified in BS 1881. These tests shall be carried out at site or in a laboratory approved by the Engineer. Two cubes shall be tested at the age of seven days and three at 28 days and the strengths determined are to comply with the standard of quality specified.  The laboratory tests shall be carried out by an independent organization, such as Government Testing Laboratory or such other undertakings approved by the Engineer.  The original test reports received from the above authorities should be submitted to the Engineer.

7.7	For all grades of concrete, the appropriate strength requirement shall be considered to be satisfied if none of the strengths of the cubes is below the specified cube strength or if the average strength of the three cubes is not less than the specified cube strength and the difference between the greatest and the least strength is not more than 20% of the average.

7.8	When the results of works cube tests show that the strength of any concrete is below the minimum specified, the Engineer may give instructions for the whole or part of the work concerned to be removed and replaced at the expense of the Contractor.  The Contractor shall bear the cost of any other part of his, or any other contractor's work, which has to be removed and replaced as a result of the defective concrete.  If any concrete is held to have failed, the Engineer may order the proportions of that class of concrete to be changed in order to provide the specified strength.

8.     	FINISHING OF FORMED SURFACES

8.1	GENERAL

8.1.1	After removal of forms, the surfaces of concrete shall be given one or more of the finishes specified below in locations designated by the Contract Documents.

8.1.2	When finishing is required to match a small sample furnished to the Contractor, the sample finish shall be reproduced on an area at least 100 Sq. ft. in an inconspicuous location designated by the Engineer before proceeding with the finish in the specified location.

8.1.3	Allowable deviations from plumb or level and from the alignment profile grades and dimensions are specified in clause 10.  Tolerances for concrete construction and defined as tolerances that are to be distinguished from irregularities in finish as described herein.  The finish requirements for concrete surfaces shall be as generally specified in this clause and as indicated on the Drawings.  Finishing of concrete surfaces shall be performed only by workmen who are skilled in concrete finishes.

The Contractor shall keep the Engineer advised as to when finishing of concrete will be performed.  Unless inspection is waived in each specific case, finishing of concrete shall be performed only in the presence of the Engineer. Concrete surfaces will be tested by the Engineer where necessary to determine whether surface irregularities are within the limits herein after specified.  Surface irregularities are classified as abrupt or gradual.

Offsets caused by displaced or misplaced form sheeting or lining or sections, or otherwise defective form lumber will be considered as abrupt irregularities, and will be tested by direct measurements.  All other irregularities will be considered as gradual irregularities, and will be tested by use of a template, consisting of a straight edge or the equivalent thereof for curved surfaces.  The length of the template will be 6.5 ft. for testing of formed surfaces and 10 ft. for testing of unformed surfaces.

8.2	AS-CAST FINISHES

Unless otherwise specified or indicated on the Drawings the classes of finish shall apply as follows:

8.2.1	Rough form finish:

No selected form facing materials shall be specified for rough form finish surfaces.  Tie holes and defects shall be patched.  Fins exceeding 1/4" in height shall be chipped off or rubbed off.  Otherwise, surfaces shall be left with the texture imparted by the forms.

8.2.2	Fair face finish:

Fair face finish applies to concrete formed surfaces, the appearance of which is considered by the Engineer to be of special importance, such as surfaces of structures prominently exposed to public inspection.  Surfaces of concrete structures requiring fair face finish is shown in the Drawings. Surface irregularities, measured as described in sub-clause 8.2.1, 'Rough form finish', shall not exceed 1/4 inch for gradual irregularities and 1/8 inch for abrupt irregularities, except that abrupt irregularities will not be permitted at construction joints. Abrupt irregularities at construction joints and elsewhere in excess of 1/8 inch and gradual irregularities in excess of 1/4 inch shall be reduced by grinding so as to conform to the specified limits. Abrupt irregularities at construction joints shall be ground on level of 1 to 20 ratio of height to length.

Unless otherwise approved, repair of imperfections in formed concrete shall be completed within 24 hours after removal of forms. The form facing material shall produce a smooth, hard, uniform texture on the concrete.  It may be plywood, temperated concrete-form-grade hardboard, metal, plastic paper, or other approved material capable of producing the desired fair face finish.  The arrangement of the facing material shall be orderly and symmetrical, with the number of seams kept to the practical minimum.  It shall be supported by studs or other backing capable of preventing excessive deflection.  Material with raised grain, torn surfaces, worn edge, patches, dents, or other defects which will impair the texture of the concrete surface shall not be used.  Tie holes and defects shall be patched. All fins shall be completely removed.

8.3   	FINISHES OF UNFORMED SURFACES

8.3.1	Monolithic Concrete Floor Finish

Where monolithic concrete floor finish is shown on the Drawings, placing shall proceed continuously for the full thickness of the course or RCC slab without change in concrete mix.  Mixing water shall be the minimum required for proper placing, and will be as specified by the Engineer.  After placing, floors, and other surfaces shall be floated with a wood float to a true surface and to elevation as shown on the Drawings.  Where indicated on the Drawings, floor surfaces shall be steel trowel finished.  Trowelling shall be the minimum amount consistent with maintaining a smooth dense surface, and shall not be done until the mortar has hardened sufficiently, to prevent excess fine material from being worked to the surface, and shall produce a dense uniform surface, free from blemishes and trowel marks.

Gradual surface irregularities shall not exceed 1/16 inch. The addition of water, dry cement, or dry cement mortar, to the surface of the concrete to facilitate finishing will not be permitted.

9.     	REPAIR OF SURFACE DEFECTS

9.1   	GENERAL

9.1.1	Any concrete failing to meet the specified strength or not formed as shown on drawings, concrete out of alignment, concrete with surfaces beyond required tolerances or with defective surfaces which cannot be properly repaired or patched in the opinion of the Engineer shall be removed at Contractor's cost. The Engineer may reject any defective concrete and order it to be cut out in part or in whole and replaced at the Contractor's expense.

9.1.2	All ties and bolt holes and all repairable defective areas shall be patched immediately after form removal.

9.2   	REPAIR OF DEFECTIVE AREAS

9.2.1	All honeycombed and other defective concrete shall be removed down to sound concrete.  The area to be patched and an area at least 6 inch wide surrounding it shall be dampened to prevent absorption of water from the patching mortar.  A bonding grout shall be prepared using a mix of approximately 1 part cement to 1 part fine sand passing No.25 BS Sieve and shall then be well brushed into the surface.

9.2.2	The patching mixture shall be made of the same material and of approximately the same proportions as used for the concrete, except that the coarse aggregate shall be omitted and the mortar shall consist of not more than 1 part cement to 2-1/2 parts sand by damp loose volume.  White Portland cement shall be substituted for a part of the gray Portland cement on exposed concrete in order to produce a colour matching the colour of the surrounding concrete, as determined by a trial patch.

9.2.3	The quantity of mixing water shall be no more than necessary for handling and placing.  The patching mortar shall be mixed in advance and allowed to stand with frequent manipulation with a trowel, without addition of water, until it has reached the stiffest consistency that will permit placing.

9.2.4	After surface water has evaporated from the area to be patched, the bond coat shall be well brushed into the surface. When the bond coat begins to loose the water sheen, the premixed patching mortar shall be applied.  The mortar shall be thoroughly consolidated into place and struck off so as to leave the patch slightly higher than the surrounding surface. To permit initial shrinkage, it shall be left undisturbed for at least 1 hour before being finally finished.  The patched area shall be kept damp for 7 days.  Metal tools shall not be used in finishing a patch in a formed wall, which will be exposed.

9.2.5	Where as-cast finishes are specified, the quantity of patched area shall be strictly limited.   The combined total of patched areas in as-cast surfaces shall not exceed 2 sq.ft. in each 1000 sq.ft. of as-cast surface.  This is in addition to form tie patches, if the project design permits ties to fall within as-cast areas.

9.2.6	Any patches in as-cast architectural concrete shall be indistinguishable from surrounding surfaces. The mix formula for patching mortar shall be determined by trial to obtain a good colour match with the concrete when both patch and concrete are cured and dry.  After initial set, surfaces of patches shall be dressed manually to obtain the same texture as surrounding surfaces.

9.2.7	Patches in architectural concrete surfaces shall be cured for 7 days. Patches shall be protected from premature drying to the same extent as the body of the concrete.

9.3   	TIE AND BOLT HOLES

After being cleaned and thoroughly dampened, the tie and bolt holes shall be filled solid with patching mortar. If architectural appearance requires, these holes may be filled partially creating the desired round clear holes pattern on surfaces exposed to view.

9.4   	PROPRIETARY MATERIALS

If permitted or required by the Engineer, proprietary compounds for adhesion or as patching ingredients may be used in lieu of or in addition to the foregoing patching procedures.  Such compounds shall be used in accordance with the manufacturer's recommendations with prior approval of the Engineer.

10.   	CONCRETE CONSTRUCTION TOLERANCES

Where tolerances are not stated in the specifications or drawings for any individual structure or feature thereof, maximum permissible deviations from established lines, grades and dimensions shall conform to the following.  The Contractor is expected to set and maintain concrete forms so as to ensure complete work within tolerance limits.  These allowable tolerances shall not relieve the Contractor of this responsibility for correct fitting of indicated materials.  These tolerances are not cumulative.

10.1   	Variation from the plumb (or the specified batter for inclined walls.)

10.1.1	In the lines and surfaces of columns, piers, walls and in arrises:

In any 10 feet of length or height     		1/4 inch

In any storey or 20 feet length        		3/8 inch

Maximum for the entire length or

height.                                			1 inch

10.1.2	For exposed corner columns, control joint grooves and other conspicuous lines.

In any bay or 20 feet maximum 			1/4 inch

Maximum for the entire length

or height                              			1/2 inch

10.2   	Variation from the level or from the grades indicated on the drawings.

10.2.1	In floors, ceilings, beams soffits and in arrises measured before removal of supporting shores.

In any 10 feet of length               			1/4 inch

In any bay or in any 20 feet length    		3/8 inch

Maximum for the entire length          		3/4 inch

10.2.2	For exposed lintels, sills, parapets, horizontal grooves and other conspicuous lines.

In any bay or 20 feet length           		1/4 inch

Maximum for the entire length          		1/2 inch

10.3	Variation of the linear building lines from established position in plan and related position of columns, walls and partitions.

In any bay or 20 feet of length        			1/2 inch

Maximum for the entire length          			1   inch

10.4	Variation in the sizes and locations of sleeves, floor

openings and wall openings.                     			+1/4 inch

10.5   	Variation in cross-sectional dimensions of columns and beams and in the thickness of slabs and walls.

Minus                                            				1/4 inch

Plus                                             				1/2 inch

10.6	Footings

10.6.1	Variation in dimensions in plan

Minus                                 			1/2 inch

Plus (plus variation applied to concrete

only, not to reinforcing bars or dowels).		2 inch

10.6.2	Misplacement or eccentricity

2 percent of the footing width in the

direction of misplacement but not more

than (applies to concrete only, not to

reinforcing bars or dowels).                   		2 inch

10.6.3	Thickness

Decrease in specified thickness        		5%

Increase in specified thickness        		No limit

10.7	Variation in Steps

10.7.1	In a flight of stairs

Rise                                				+ 1/8 inch

Tread                               				+ 1/4 inch

10.7.2	In consecutive steps

Rise                                				+ 1/16 inch

Tread                               				+ 1/8 inch

10.8	Tolerances for Pre-cast concrete construction

Forms must be true to size and dimensions of concrete members shown on the plans and be so constructed that the dimensions of the finished products will be within the following limits at the time of placement of these units in the structure, unless otherwise noted on structural-architectural drawings:

10.8.1	Overall dimensions of members          		1/16 inch

per 10 feet

10.8.2	Cross-sectional dimensions

Sections less than 3 inch.             		1/16 inch

Sections over 3 inch and

less than 18 inch.                      			1/8 inch

Sections over 18 inch.                  			1/4 inch

10.8.3	Deviations from straight line

in long sections.

Not more than 					1/8 inch

per 10 feet.

10.8.4	Deviation from specified camber			+ 1/16 inch per

10 feet span.

Maximum differential between adjacent

units in erected position 				1/4 inch

11.    	ACCEPTANCE OF STRUCTURE

11.1  	GENERAL

11.1.1	Completed concrete work which meets all applicable requirements will be accepted subject to the other terms of the Contract Documents.

11.1.2	Completed concrete work which fails to meet one or more of the requirements and which has been repaired to bring it into compliance will be accepted subject to the other terms of the Contract Documents.

11.1.3	Completed concrete work which fails to meet one or more of the requirements and which cannot be brought into compliance may be accepted or rejected as provided in these Specifications or in the Contract Documents.  In this event, modifications may  be required to assure that remaining work complies with the requirements.

11.2  	DIMENSIONAL TOLERANCES

11.2.1	Formed surfaces resulting in concrete outlines smaller than permitted by the tolerances of clause 10 shall be considered potentially deficient in strength and subject to the provisions of sub clause 11.4.

11.2.2	Formed surfaces resulting in concrete outlines larger than permitted by the tolerances of clause 10 may be rejected and the excess material shall be subject to removal.  If removal of the excess material is permitted, it shall be accomplished in such a manner as to maintain the strength of the section and to meet all other applicable requirements of function and appearance. Permission is required if excess material is to be removed in accordance with this clause.

11.2.3	Concrete members cast in the wrong location may be rejected if the strength, appearance or function of the structure is adversely affected or if misplaced items interfere with other construction.

11.2.4	Inaccurately formed concrete surfaces exceeding the limits of Clause 10 or of Clause 6.1.6 of Section 'Formwork' and which are exposed to view, may be rejected and shall be repaired or removed and replaced if required.

11.3  	APPEARANCE

11.3.1	Architectural concrete with surface defects exceeding the limitations of Sub-clause 6.1.6 of the Section, 'Formwork' shall be removed and replaced.

11.3.2	Other concrete exposed to view with defects which adversely affect the appearance of the specified finish may be repaired only by approved methods.

11.3.3	Concrete not exposed to view is not subject to rejection for defective appearance.

11.4	STRENGTH OF STRUCTURE

11.4.1	The strength of the structure in place will be considered potentially deficient if it fails to comply with any requirements, which control the strength of the structure, including but not necessarily limited to the following conditions.

-	Concrete strength requirements not considered to be satisfied in accordance with Clause 6 hereof.

-   	Reinforcing steel size, quantity, strength, position or arrangement at variance with the requirements as listed under specification of 'Reinforcement' or in the Contract Documents.

-   	Concrete which differs from the required dimensions or location in such a manner as to reduce the strength.

-   	Curing less than that specified.

-   	Inadequate protection of concrete from extremes of temperature during early stages of hardening and strength development.

-   	Mechanical injury, construction fires, accidents of premature removal of formwork likely to result in deficient strength.

-   	Poor workmanship likely to result in deficient strength.

11.4.2	Structural analysis and/or additional testing may be required when the strength of the structure is considered potentially deficient.

11.4.3	Core tests may be required when the strength of the concrete in place is considered potentially deficient.

11.4.4	If core tests are inconclusive or impractical to obtain or if structural analysis does not confirm the safety of the structure, load tests may be required and their result evaluated in accordance with British Standard BS 8110 or ACI Standard 318.

11.4.5	Concrete work judged inadequate by structural analysis or by results of a load test shall be reinforced with additional construction if so directed by the Engineer or shall be replaced, at the Contractor's expense.

11.4.6	The Contractor shall pay all costs incurred in providing the additional testing and/or analysis required by this section.

11.4.7	The Employer will pay all costs of additional testing and/or analysis which are made at his request and which is not required by these Specifications, or by the Contract Documents.

11.5	Testing of Material

a)	All tests shall preferably be done at site. Only the test which are not possible to be carried out in the site laboratory shall be referred to the laboratory approved by the Engineer. All testing charges thereof shall be borne by the Contractor.

For testing of reinforcement steel bars, the samples shall be referred to the laboratory approved by the Engineer at the cost of the Contractor.

b)	Cement shall be tested as prescribed in ASTM C -150.

c)	Aggregates shall be tested as prescribed in British Standard BS 812 & 882. In addition fine aggregate shall be tested for organic impurity in conformance with ASTM Standard C.40.

12.	MEASUREMENT AND PAYMENT

12.1 	General

Except otherwise specified herein or elsewhere in the Contract Documents, no measurement and payment will be made for the under mentioned specified works related to the relevant items of the Bills of Quantities. The cost thereof shall be deemed to have been included in the quoted unit rate of the respective items of the Bills of Quantities.

The rates quoted by the Contractor in the Bill of Quantities shall include work to be executed under these specification in any floor and at any height except where otherwise specifically stated in the relevant item of Bill of Quantities and the Contractor shall not be entitled to any claim or claim any compensation on this account.

12.1.1	Providing, fixing, striking, etc. of formwork.

12.1.2	Providing, placing and fixing of anchor bolts or any other embedded parts.

12.1.3	Providing and installing all type of joints in concrete structure, including expansion joints.

12.1.4	Providing and fixing water stoppers.

12.2	Plain and Reinforced Concrete

12.2.1	Measurement

Concrete shall be measured as executed but no deduction shall be made for the following:

-   	Volume of any steel embedded in the concrete.

-	Volume occupied by water pipes, conduits etc. not exceeding 10 square inches each in cross-sectional area.

-   	Voids not exceeding 4 square inch in work given in square feet. If any void exceeds 4 square inch, total void shall be deducted.

Voids, which are not to be deducted as specified above, refer only to openings or vents which are wholly within the boundaries of measured areas.

Openings or vents which are at the boundaries of measured areas shall always be subject to deductions irrespective of size.

Concrete work shall be classified and measured separately as listed under items of Bills of Quantities.

Junction between straight and curved works shall in all cases be deemed to be included with the work in which they occur.

Measurement of walls shall be taken between attached columns piers or pilaster.  The thickness of attached columns, piers or pilaster shall be taken as the combined thickness of the wall and the columns, piers or pilaster.

Attached or isolated columns, piers, pilaster, and the like (except where caused by openings) having a length on plan not exceeding four times the thickness shall be classified as columns.  Those having a length over four times the thickness and are caused by openings in wall shall be classified as walls.

Columns shall be measured from the top of footing/footing beams or floor surfaces to the underside of beams or slabs as the case maybe.  Where the width of beams is less than the width of columns, the extra width at the junction shall be included in the beams.

The depth of the beams shall be measured from bottom of the slab to the bottom of the beams except in case of inverted beams where it shall be measured from top of slab to the top of beam.  The cross-section of the beam shall be the actual cross-section below or above the slab.

Measurement of acceptably completed works of plain and reinforced cement concrete will be made on the basis of number of cubic feet of concrete placed and compacted in position within the neat lines of the structure as shown on the Drawings or as directed by the Engineer.

Measurement of curing agents/chemicals/admixtures for plain & reinforced concrete will be made on the basis of amount of agents/chemicals/admixtures required in litres as per manufacturer’s recommendation for the area being treated.

12.2.2	Payment

Payment will be made for the acceptable measured quantity of plain and reinforced cement concrete on the basis of unit rate per cubic feet quoted in the Bills of Quantities and shall constitute full compensation for all the works related to the item.

Payments will be made separately for the quantity of curing agents/chemicals/admixtures being used for concrete works only after written approval of The Engineer.