SECTION 5220

- VALVES

- SCOPE

- APPLICABLE STANDARDS

- SUBMITTALS

- MATERIAL AND EQUIPMENT

- DELIVERY, STORAGE AND HANDLING

- TESTING AND COMMISSIONING

- MEASUREMENT AND PAYMENT

1.	 SCOPE

The work under this section of the specification consists of furnishing all plant, labour, equipment, appliances, materials and performing all operations required as specified herein, as shown on the drawings, or as directed by the Engineer, in connection with installation of valves.

2. 	APPLICABLE STANDARDS

Bronze gate valves		BS- 1952

Bronze check valves		BS- 5152

Float valves			BS- 1212

- SUBMITTALS

The contractor shall submit technical brochures and samples of all the items mentioned in the Specifications from approved manufactures or as directed by the Engineer

- MATERIAL & EQUIPMENT

4.1	DESCRIPTION

All valves shall be of renowned manufacturer as specified. Valve material shall be suitable for installation on potable water lines, sewage line or sludge piping. Service rating of the valves shall be at least 7 bars to 13 bars. The interior of all valves shall be cleaned of all foreign material before installation.

Valves shall be installed at the position indicated in the Contract Documents or as directed by the Engineer. Valves shall be adequately supported. Installed valves shall be subjected to pressure and leakage tests and no leakage shall be observed under these tests. End joints, flanges, etc., shall be of the appropriate class and material.

Valves shall be installed either in chambers or above grade on line as shown in the Contract documents and/or as specified herein. Valves shall be securely anchored.

Open and closed position indicator shall be provided for all valves. If installed in valve chambers, the indicator shall not extend above ground and shall not interfere with opening or closing of the valve. The indicator design shall be approved by the Engineer before installation.

4.2	BRONZE GATE VALVE

All gate valves shall be of bronze conforming to BS-1952 and shall be of 16 bars for the working pressure. Open and shut indicators shall be marked on the handle. The ends may be screwed or flanged. The valves are to be installed inclusive of all fittings and accessories required for complete installation.

4.3	BRONZE CHECK VALVES

Check valves shall conform to B.S. 5152 "Specifications for bronze check valves for general purposes". The service rating shall be 16 bars. The direction of flow shall be permanently marked on the body of the valve. Body of valve shall be tested to 1-1/2 times the service rating and seat shall be tested to service rating. No leakage shall be permitted under the above tests check valves shall be of swing type.

End of the valves shall be flanged to joint with the standard fittings. Flanges shall be of appropriate class and material. Valves shall be installed at positions shown on the drawings the interior shall be cleaned of all foreign matter before installation. They shall be inspected to ensure that all components are sound and in working condition.

4.4	AIR VALVES

Air valves shall be of cast iron, of specified size for automatic discharge of air and for automatic breaking of vacuum in a pressure main. They shall be suitable for installing on water mains of 7 bars working pressure. The material used shall be corrosion resisting, growth. Each valve shall be installed with an isolating gate valve, stand pipe, clamp and connection with the line.

4.5	FLOAT VALVE

Float valve shall be of copper alloy, piston type and shall conform to B.S. 1212. Float shall be of copper and shall conform to B.S. 1968.

- DELIVERY, STORAGE & HANDLING

Valves should be handled and stored properly to avoid any damage and slippage of threads especially during installation.

- TETESTING & COMMISSIONING

Valves shall be tested to ascertain their proper working under test and working pressures.

7. 	MEASUREMENT AND PAYMENT

7.1 	MEASUREMENT

Measurement of acceptably completed works of valves, will be made on the basis of actual number of valves installed in position as shown on the Drawing or as directed by the Engineer including jointing arrangement of pipe on both end of valves gaskets, nuts, bolts, etc., anchoring of valve in concrete, steel embedded parts and indicators, wire mesh screen on washout and Painting.

7.2	PAYMENT

Payment will be made for acceptable measured quantity of valves, on the basis of unit rate per number quoted in the Bill of Quantities and shall constitute full compensation for all the works related to the item.