SECTION - 8121

DISTRIBUTION POWER TRANSFORMERS

1.0	SCOPE

The work under this section consists of supplying, installing, testing, connecting and commissioning of all materials and services of the complete Distribution Power Transformers as specified herein, or as given in the Tender Drawings and in the Bill of Quantities.

The Contractor shall discuss the electrical layout with the Engineer and co-ordinate at site with other services for exact location and position of the equipment.

The Distribution Power Transformers with accessories shall also comply with the General Specifications for Electrical Works, Section-8001 and with other relevant provisions of the Tender Documents.

2.0	GENERAL

The capacity of transformers to be provided are shown on the drawings and mentioned in Bill of Quantities. The transformers shall be complete, with all accessories and attachments as detailed in these specifications or otherwise required for satisfactory service.

All pertinent details, drawings, data, etc.  shall be provided to the Engineer for approval prior to manufacturing. The transformers shall be manufactured in conformity with the requirements of concerned power supply utility company such as KESC, WAPDA, IESCO/ PESCO, etc. so that approval of power supply connection can be obtained.

Transformers built to these specifications and the standards given in this section or other relevant standards approved by the Engineer will be acceptable.

3.0	APPLICABLE STANDARDS/CODES

The following standards and codes shall be applicable for all materials in scope of this section: -

IEC 60076-1  	-	Power transformers – Part 1: General

IEC 60076-2	-	Power transformers – Part 2: Temperature rise

IEC 60076-3	-	Power transformers – Part 3: Insulation levels and

dielectric tests

IEC 60076-3-1		Power transformers external clearances in air

IEC 60076-5	-	Power transformers – Part 5: Ability to withstand

short circuit

BS  148 	-  	Transformer oil

BS  223 	-  	High voltage bushings

4.0	MATERIAL

4.1	Power Transformer Construction

The transformer tank shall be constructed of welded boiler plates and provided with external radiating tubes. The tank and radiating tubes shall be designed to withstand, without developing any deformation, pressure at least 25% greater than the maximum operating pressure.   The steel cover plate shall be bolted to the tank-using gasket for perfect oil seal. Inspection hole with cover shall be provided on top of the tank. Two earth terminals shall be provided diagonally at the base of the transformer tank. The transformer shall be anti-corrosive painted and finished in grey colour.

The oil preservation system shall have a conservator tank fitted with silica gel breather and oil level indicator.

The transformer core shall be built of non-aging, cold rolled, electrical silicon steel lamination and each lamination insulated to reduce eddy current   losses.  The core laminations shall be clamped   and   bolted effectively to reduce humming.

The winding coils shall be of high-grade electrolytic copper conductor, flat or round, paper insulated, thoroughly dried and impregnated as required.

The high tension (HT) lead on Distribution transformer shall be brought out to glazed porcelain insulator bushings for external connections to cables. Protective arcing horn spark gaps shall be provided on H.T bushings to protect the transformer from surge voltages.

The three LT and neutral phase leads shall be brought out and terminated at glazed porcelain insulator bushings for connection to LT side by copper bus-duct or cables.

Off-load tap changer shall be provided on HT side at suitable location preferably on the side of transformer tank. A clear marking, illustrated by diagram, shall be provided to indicate the tap positions.

Double float Buchholz relay shall be provided on the transformer. It shall have required number of contacts for connection to tripping and alarm circuits.

4.2	Principal Data of Power Transformers

The transformers shall be fully tropicalized, three phase, step down, oil filled, self cooled, core type, double wound, suitable for parallel operation.

The transformers shall meet the following specifications:

-    	Capacity (Rated continuous 	:    	As stated on drawings

output at full load)      			and BOQ

-    	Voltage ratio at no-load	:    	11000/415 Volts

-    	Frequency                		:    	50 Hz

-    	Vector group             		:    	Dyn 11

-    	Off load tapping arrangement :    	+2.5%, -5%, -7.5%

on HT side

-    	HT connection          		:    	11 kV Delta

-    	LT connection           		:    	415 V with grounded star point.

-    	Neutral on LT side      	:    	Brought out & solidly earthed

-    	Temperature rise of oil	:    	40oC  maximum

over ambient temperature

-    	Temperature rise of winding  :    	50oC  maximum

over ambient temperature

-    	Impedance voltage        	:    	7%

-    	Voltage regulation for   	:    	Not to exceed 2.5% of

rated operating condition       		no-load secondary voltage

at 85% power factor

-    	Rated maximum voltage 	:  	15 kV / 0.6 kV

HT/LT

-    	Rated short-time current 	:    	Equal  to the rating of

associated HT Switchboard.

-	Rated Basic Impulse Level 	:	95 kV

(BIL)

-	Cooling			:	mineral oil immersed natural

cooled type (ONAN)

The design data to be furnished by the Contractor for approval of the Engineer shall include, but not be limited to, the following:

-	Iron losses.

-	Copper losses.

-	Rated short-time current.

-	Switching in-rush current.

-	Efficiencies at different loads.

-	Voltage regulation

-	Type and quantity of oil for complete filling of transformer.

-	Transformer weight.

4.3	Accessories

In addition to the standard accessories of the power transformers as offered by the manufacturer, the transformers shall also be provided with following accessories: -

-	Oil drain plug.

-	Bi-directional rollers.

-	Lifting lugs.

-	Dial type thermometer with maximum temperature indicator and two adjustable normally open contacts for temperature alarm and tripping.

-	Stainless steel diagram and rating plate according to IEC-60076.

-	Pressure release safety valve.

5.0	INSTALLATION

Transformers shall be installed in kiosk type substation as shown on drawings. All civil works, including provision of cable trench, transformer oil pit, openings in wall, steel channel, etc., shall be carried out under civil works. The Contractor shall be responsible for general checking and co-ordination with civil works to ensure compliance with the requirements of transformer manufacturer for installation of equipment. For installation, connecting, testing and commissioning of transformers, the Contractor shall provide all required labour, materials, tools and testing equipment.

The transformer installation shall be carried out in accordance with specifications and the best-accepted practice. Any loose components supplied by manufacturer shall be assembled, installed and connected in place as to form a complete assembly as per manufacturer’s instructions. After the transformers are placed in position and aligned for HT & LT terminations, the roller wheels shall be locked with the foundation steel channel to avoid any unintentional movement of the wheels.

The HT cable shall terminate at the flange terminals on the HT side. The supporting channels, fixing material, etc., required for HT cable shall be furnished by the Contractor, details of which shall be approved by the Engineer prior to installation. The cable end box/termination kit will be supplied with the cable.

After the transformers are installed and connected, a thorough check shall again be made for the proper fixing of accessories, neutral connections, oil level, etc. The transformers shall be tested before energizing as per instructions contained in the article “Testing” of General Specifications for Electrical Works, Section – 8001 of these Specifications.

6.0	MEASUREMENT AND PAYMENT

6.1	General

The Contractor’s bid amount against each Bill of Quantities item as given below shall include supply, installation, testing, commissioning   and completion for all work specified herein and/or as shown on the Tender Drawings related to the item.

6.2	Distribution Power Transformers

6.2.1	Measurement

Measurement shall be made for each size of Distribution Power Transformer as given in BOQ acceptably supplied and installed by the Contractor, as a complete Job.

6.2.2	Payment

Payment shall be made for the number of Jobs measured as provided above at the Contract unit price each and shall constitute full compensation for supplying, installing, connecting, testing, commissioning and completion of the Power Transformer with all accessories including control wiring to the HT / LT switchboard.