SECTION - 8132

LT SWITCHBOARDS

1.0	SCOPE OF WORK

The work under this section consists of supplying, installing, testing, connecting,  commissioning of all material and services of  the complete LT Switchboards as specified herein and/or shown on the Tender Drawings and given in the Bill of Quantities.

The Contractor shall discuss the electrical layout with the Engineer and coordinate at site with other services for exact location and position of the LT Switchboards.

The LT Switchboards shall also comply with the General Specifications for   Electrical Works Section-8001 and with other relevant provisions of the Tender Documents.

2.0    	GENERAL

The LT Switchboards shall be of sheet steel fabricated, floor mounting, cubicle type, totally enclosed, dust tight and vermin proof. It shall be complete in all respect with material and accessories, factory assembled, tested and finished all according to the specifications and to the normal requirements.

The switchboard with all components and accessories shall be suitable for front operation only and shall:

-	have a rated service short circuit breaking capacity, (Ics) conforming to IEC 60947-2 as shown on the drawings.

-	be  provided with adequate clearance from live parts so  that flashovers cannot be caused by switching, vermin, pests, etc.

-	have all  components rated for insulation class of 600-volts minimum.

-	be  designed  for flush mounting of all  instruments  on  the front side.

-	have  all  incoming and outgoing connection from the  top  or  bottom as per requirement of site conditions.

-	have the components mounted so as to  facilitate  ease  of maintenance from the front.

-	have common lamp test facility for all lamps.

-	have wiring diagram in the pocket on the inside of each door of the panel.

-	be suitable  for  415 volts  AC, 3 phase  4 wire,  50 Hz  system.

-	be  labeled with stainless steel nameplate on the front side of  door for each incoming and outgoing circuit.

-	have doors grounded by flexible copper cable/strip.

-	have arrangements for extension of panel in future.

-	have Programmable Logic Circuit (PLC) equipment for controls, interlocking with manual by-pass switch which shall be utilized in case of PLC equipment maintenance/failure.

3.0    	APPLICABLE STANDARDS/CODES

The  latest editions of the following standards and codes  shall  be applicable  for  the materials specified within the  scope  of  this Section :

BS     3871  		- 	Miniature & moulded Case Circuit Breaker.

IEC    60947-2	 	- 	Low Voltage Switch gear and Control gear.

IEC    60439-1		- 	Low Voltage Switchgear and Control gear 						Assemblies.

IEC    60408   		- 	Low   Voltage   Air   break  Switches,  Air  Break

Disconnectors, Air break Switch Disconnectors and 					Fuse Combination Units.

BS      1432		-	Bus Bars.

BS      88      		- 	HRC Fuses.

BS      89/90   		- 	Ammeters and Voltmeters.

IEC    60070   		- 	Power Capacitors.

BS     3938    		- 	Low Voltage Current Transformers.

IEC   60073		-	Colours for indicator lights and push buttons.

4.0    	MATERIAL

4.1    	Sheet Metal Work

The LT switchboards shall be fabricated, welded, grinded, finished with angle iron framework and cladded with 14 SWG MS sheet. It shall be suitably divided into panels and compartments for accommodating the required number of circuit components, instruments and accessories.

The switchboard shall be supplied complete with foundation bolts and other installation materials as recommended by the manufacturer. Proper size cable clamping channels with galvanized steel clamps and brass cable glands respectively for unarmoured and armoured cables shall be provided. All holes, cutout shall be tool or jib manufactured and free from burrs and rough edges. An earth bar of appropriate cross section shall be provided and connected to the bodies of all sections of the switchboard. Two external earth terminals shall be provided for main earth connection to the body of switchboard.  The doors shall be earthed by means of flexible copper strip. Means shall be provided to limit the opening angle of doors to about 1000.

The cabling inside the switchboard shall be suitably numbered and harnessed  by means of straps or cords. Colour sleeves shall be provided on each cable lugs, connected to the bus bars, circuit breakers or terminals etc. for phase identification. Wiring to door mounted components shall be in flexible PVC conduit.  All indicating, selecting and control equipment shall be suitably arranged and clearly labelled by means of flame proof material using indelible ink/marking indicating the rating of fuse, switches, etc. The nameplates provided on the front of panel shall be of flame retardant material preferably stainless steel. Use of plastic or any inflammable material shall not be permitted for nameplates.

All metalwork of the switchboards shall be cleaned down to bare shining metal phosphated and the surfaces chemically prepared for powder coating. Then these shall be coated with powder of colour RAL 7032 and then baked in oven.  The thickness of powder coating shall not be less than 120 microns.

4.2    	Components

The switchboards shall be provided with all components as specified or shown on the Drawings and as necessary for the satisfactory operation of the switchboard and of the electrical system. Typical specifications are given hereunder.

4.2.1  	Bus Bars

The bus bars shall be made of high conductivity electrolytic  tinned copper and shall be completely  isolated and mechanically braced for the specified fault level. The  phase  identification  of bus bars  shall  be  by providing colours  sleeves on bus bars ends and these shall be  red, yellow and blue for phase and black for  neutral.  The earth bus bar shall be green.

The  bus  bars  shall be triple pole, neutral & earth and shall  be of appropriate size to meet the electrical and mechanical  requirements of the system. The temperature rise shall not exceed 30 degree centigrade at rated current.

Neutral bus bar shall be of the same cross section as phase bus bars. Earth bus bar shall be of half cross section area as phase bus bars.

4.2.2  	Circuit Breakers

The circuit breaker shall be triple or four pole, manually operated or motor operated, spring charged type as shown on the drawings with front drive grip handle. ON-TRIP-OFF indication shall be provided on circuit breakers. The all circuit breakers shall have the following protections and setting range unless                      otherwise shown on the drawings:

-  	Adjustable three pole, manual reset thermal overload release of setting range 80 to 100% of rated current.

- 	Magnetic triple pole short circuit release having range according to manufacturer's standard range.

The incoming circuit breakers of main LT panel (normal and  emergency) shall be air circuit breakers  whereas outgoing circuit breakers shall be moulded case  type, unless stated otherwise on the drawings.

The incoming circuit breaker shall have two numbers normally open and two numbers normally closed auxiliary contacts rated for 2 Amp, 230 VAC.  The incoming circuit breaker shall also have ON-TRIP-OFF indicating lamps. Where shown on the drawings indication lamps shall also be provided for outgoing circuit breakers. The circuit breaker shall have specified rupturing capacity without the use of back-up fuses. Auxiliary release and trip coils shall be provided for desired operation and/or interlocking as stated on   the drawings.

The motor operated, spring charged  type   circuit breakers  shall be provided with anti-pumping  circuit to prevent repeating cycle of TRIP reset  and ON  even if  the  close  command is  given  while  the  circuit breaker has tripped due to fault.

Wherever withdrawable type LT switchboard is specified on the drawings/BOQ, the switchboards shall also comply with the following requirements:

- All circuit breakers and switch fuse units shall be as shown on the drawing. Where two or more feeders are contained in the same cubicle, they are to be separated by barriers of steel or fire resistant insulating material. If required, the metal surface of the cubicle shall be protected by fire resistant insulating material. Each panel shall combine in tier form all respective components with their incoming and outgoing power feeders.

- The draw out switching units shall be mounted on trucks or slide-in chassis having adequate guidance by greased sliding rails and/ or rollers. They shall be connected to the bus bars by means of a self-aligning plug and socket arrangement and complete isolation of each circuit shall be attained by drawing out the switching unit.

- The main contacts shall have safety shutters, which will automatically cover the line contacts as the circuit breaker is withdrawn. The withdrawal of circuit breaker shall be accomplished by means of a crank, with as little effort as possible.

- The contact surfaces of the plugs and sockets shall be silver-plated. The contacts shall be ample sized and sufficiently strong to withstand maximum prevailing short circuits and carry continuously their normal rated currents without damage or overheating of any kind.

- Also, the control circuits shall be provided with plugs and sockets.

-	The withdrawable units shall have clearly marked service, test and isolated (ready for complete withdrawal) positions. A mechanical interlock is to be provided to prevent withdrawal of the unit unless the power circuit has been interrupted. The unit shall, furthermore, positively be locked in the test position before it is manually released for complete withdrawal.

4.2.3  	Switch - Fuse Units

The switch-fuse unit shall comprise a triple pole on load isolating switch with HRC fuses.  The fuse shall be supplied complete with the fuse base and shall conform to BS-88 Class Q1 with a fusing factor of 1.5.

4.2.4	Three Phase Energy Meters (Kilowatt Hour Meters)

Three phase energy meters of frequency 50 Hz and accuracy class of 1.0 with proper meter base, cover, frame, terminal block, terminal cover, auxiliary circuit etc. shall be provided for use with instrument transformers. The meter shall be approved by WAPDA/IESCO.

The construction of meter shall be suitable for its purpose in all respect and shall give reasonable assurance of permanence in all mechanical, electrical and magnetic adjustments. The construction shall be such that the meter is not prone to produce appreciable noise in use.

The meter shall have a dust proof case, which can be sealed in such a way that the mechanism of the meter is only accessible after breaking the seal. The case shall be made of metal or toughened glass of a sufficient strength to ensure adequate protection of the internal parts.

The direction of rotation shall be marked by a clearly visible indelible arrow.

Electronic meters with same accuracy class can also be provided subject to no additional cost and approval from WAPDA/IESCO.

Any test(s) to confirm accuracy and confirmation of requirements of specifications and WAPDA/IESCO shall be made. No additional payment shall be admissible for all such tests and is deemed to be included in the cost of the equipment.

4.2.5  	Ammeters and Voltmeters

All meters shall be flush mounting, moving iron, spring controlled. The front dimensions shall be 96 x 96 mm for meters.

The meters shall be of accuracy class 1.5 according to BS-89  and  90.  The  ammeter shall  be  suitable  for connection to 5 Amps secondary of current transformers or directly through shunt as shown on  drawings. The ammeters and voltmeters shall have measuring range  as indicated  on  the  drawings.

4.2.6  	Current Transformers

Air-cooled, ring type current transformers shall be provided having transformation ratio as indicated on the drawings.  The current transformers shall be of suitable burden having accuracy class 1.0 according to BS  3938.  The current transformers shall have 5 amps secondary.

4.2.7  	Selector Switches

Ammeter and voltmeter selector switches shall be complete with front plate and grip handle. R-Y-B and OFF position for ammeters and RY-YB-BR-RN-YN-BN and OFF position for voltmeters shall be marked on the respective selector switches.

The selector switches for controls shall be rotary cam type, having required number of positions. It shall be provided complete with knob and front  plate  showing  all positions as required.

4.2.8  	Air Break Contactors

The contactors shall be air break, triple pole 415 VAC type  and  suitable for the type of duty (at least utilization Category AC3) to be performed.  The main contacts shall be silver  tipped, butt  type with double break per pole. Each contactor shall be provided with single phase 230 VAC operating coil and minimum one spare normally open and one normally closed auxiliary contact. The number of working auxiliary contacts shall be provided according to the system requirements.

4.2.9 	Push Buttons

The push buttons shall be illuminated, momentary make/break contact type or latch type (push-on/push-off) as required and approved by the Engineer and suitable for flush mounting. The push button for ON and OFF switching shall be red and green respectively. They shall be provided as shown on the drawing.

4.2.10  HRC Fuses

HRC  fuses shall be provided complete with fuse bases, fuse etc. The fuses shall have a fusing  factor  as specified for class Q1 in accordance with BS 88.

4.2.11 	Indicating Lamps

Indicating lamps shall be LED type having long life suitable for flush mounting, complete with base. They shall be suitable for operation on 230 V AC and shall have rosettes of suitable colours as approved by the Engineer.

4.2.12 	Line up Terminals

Line up terminals wherever provided for control or power circuits shall be suitable for voltage and size of conductors as indicated on drawing.

The line-up terminals for controls shall be suitable for channel mounting.  All necessary accessories such as end plates, fixing clips, transparent label holder caps and label sheets with marking shall be provided.

4.2.13 	Power Factor Improvement Plant

The power factor improvement plant if used shall be utilized for improving the power factor of the system on 415 volts side. The plant shall be automatic-cum-manual.

The power factor improvement plant shall be aligned with the Main LT Switchboard. The control panel for the plant shall be a part of Main LT Switchboard, whereas the power factor correction capacitors shall be mounted in a ventilated panel. The capacitors shall be suitable for three phase, 415 volts, 50 Hz system and shall be self cooled, designed for indoor use in tropical climate for maximum ambient temperature as specified in section-8001, General Specifications for Electrical Works. The capacitors shall be in the form of banks divided for required stages. Each capacitor bank unit shall be of kVAr capacity as shown on drawings at 400V. Each capacitor unit shall be complete with discharge resistors and internal fuses and shall be connected with control panel with proper size of single core PVC insulated cables.

The control panel of the plant with all accessories shall be installed within LT Switchboard. The panel shall be supplied complete with a set of 3-phase, full capacity, insulated copper busbars, interconnections, risers, designation labels, cable sockets, holdings down bolts, wiring with cleats and ferrules, earthing sockets and studs, etc. The control panel shall at least accommodate, but not limited to the following:

- 	1 No. Multi-stage power factor correction relay for automatic/manual control.

-    	1  No.  3-phase, 4  wire, 415  volts,  unbalanced load power factor indicator.

-    	1 No.  Current transformer with 5 amps  secondary current,   having  suitable  output  burden   and accuracy.

-    	3 Nos. Instrument potential MCB.

Following equipment shall be provided for every capacitor bank:

-    	1 No.  Triple   pole   415 volts air break contactor with auxiliary contacts (40/75/125 amps for 12.5/25/50 kVAr bank respectively).

-    	1 Set 3 Nos. HRC back-up fuses with base and carrier having the fuse factor as required for capacitors in accordance with BS - 88  (40/75/125 amps for 12.5/25/50 kVAr bank respectively).

-    	1 No.  Auto-Off-Manual selector switch.

-    	1  No.   Red  lamp for  'ON'  indication  of  the contactor.

4.2.14	Surge Protection

Surge Arresters shall be provided in LT switchboard, wherever required, as shown on drawing. The 415 Volts surge arrester shall have the following characteristics:

-	Voltage Class (highest system voltage):	440 V rms

-	Service (rated voltage): 			415/1.732 V rms

-	Peak Current surge:				40 kA

This equipment will be tested in accordance with the relevant IEC Standard.

5.0    	INSTALLATION

The LT Switchboard shall be installed at location shown on the drawing. The concrete pedestal shall be constructed as part of civil works.  The Contractor shall ensure co-ordination with the civil works for providing any openings, holes, etc to avoid any breakage to completed works.  In case the provisions in civil works for installation of electrical equipment are not made or made incorrect the same shall be rectified by the Contractor at his own cost and to the satisfaction of Engineer.

The Contractor shall provide foundation bolts and grout them in cement concrete floor using non-shrinkable material with the approval of Engineer.

All installation materials for physically erecting the switchboard, such as bolts, nuts, washers, supporting steel, etc., shall be provided and installed by the Contractor. The switchboard, manual transfer switch and outdoor feeder pillar shall be installed upright and in level and shall be firmly and rigidly bolted to the floor and concrete supports.

The LT Switchboard shall be completely erected as per manufacturer's instructions and as approved by the Engineer. Loose parts dispatched by the manufacturer shall be installed and connected as per assembly drawing provided by the manufacturer. Any safety locking of meter, relays, etc., provided by the manufacturer for safe transport shall be released only after the switchboard is erected in position. The incoming and outgoing cables shall be connected as recommended by cable manufacturer and providing colour sleeve on the lugs at both ends of cables the cable armour shall be connected effectively to ground.

The LT Switchboard body shall be connected to earth as per instructions given in section "Earthing" of these Specifications. The switchboard shall be tested and commissioned in the presence of the Engineer.

The LT Switchboard shall be tested before energizing as per instructions    contained in article "Testing" of General Specifications for Electrical Works, Section-8001 of these Specifications.

6.0    	MEASUREMENT AND PAYMENT

6.1    	General

The Contractor's bid amount against Bill of Quantities item as given below shall include design, fabrication, supply, installation, testing, commissioning and completion for all works specified herein and as shown on the Tender Drawings related to the item.

6.2    	Low Tension Switchboards

6.2.1  	Measurement:  Measurement shall be made for the complete job of each LT Switchboard as shown on drawing and given in BOQ acceptably supplied and installed by the Contractor as a complete job.

6.2.2  	Payment:   Payment shall be made for the total  number of  each type of job measured, as provided above,  at the Contract unit price each and shall constitute full compensation for design,  supplying, installing, connecting, testing and commissioning of the LT Switchboard as per single line diagram  shown on  the drawing including power factor improvement plant, PLC equipment for interlocking alongwith manual bypass arrangement, all erecting material such as foundations bolts, supporting steel channels,  nuts,  washers, cable glands etc.