SECTION - 5100

# PLUMBING

- SCOPE

- APPLICABLE STANDARDS

- SUBMITTALS AND SHOP DRAWINGS

- MATERIAL AND EQUIPMENT

- EXECUTION

- TESTING AND COMMISSIONING

- MEASUREMENT AND PAYMENT

1. 	SCOPE

The work under this section consists of providing all material and equipment and performing all the work necessary for the complete execution (jointing, clamping, cleaning, painting etc. both above and underground and embedded in walls) and completion, including testing and commissioning of all systems of plumbing works as shown on the Drawings and/or as specified herein and/or as directed by the Engineer. The system include plumbing works as follows:

- Cold and Hot Water Supply

- Fire Protection System

- Building Drainage

- Rain Water Drainage

All the above named systems shall be completed in all respects including extension of these internal systems upto the specified limits outside the building as indicated on the drawings.

- APPLICABLE STANDARDS

G. I. Pipes					BS- 1387 (1985) Medium duty

G.I. & M.S Pipes				API 5L WALL B Standard ERW Sch. 40

Polypropylene Random (PPR) pipes		DIN 8077-78

C. I. Spun Pipes				BS- 416

uPVC Pipes					ISO- 3633 Class-B & BS- 4514/5255 Type-A

- SUBMITTALS & SHOP DRAWINGS

All the materials and equipment shall be of the specifications mentioned herein and the Contractor shall submit the sample, necessary catalogues, sketches, the name of manufacturer and guarantee if necessary, before installation. The system shall be installed after the Engineer approves it. All material and equipment shall be new and unused.

It is specifically intended and must be agreed to by each Contractor submitting a bid, that any material or labor which is usually furnished as a part of such equipment and which is necessary for its proper completion and best operation shall be furnished as a part of this Contract without any additional cost whether or not shown in detail on the drawings or described in detail, in the specifications.

Approval of material and equipment by the Engineer shall not absolve the Contractor of the responsibility of furnishing the same of proper size, quantity, quality and all performance characteristics to efficiently fulfill the requirements and intent of the Contract Documents.

Prior to commencement of works on site and at least 3 weeks in advance of all the drawing being required for actual execution the Contractor shall submit on larger scale as approved by Engineer, shop drawings in triplicate for approval to the Engineer. The Engineer shall review the drawing and (i) approve the drawing or, (ii) approve the drawing with comments or, (iii) disapproved the drawings with comments for rectification/revision of the drawing and resubmit 3 copies to the Consultant for approval. On a drawing being approved, the Contractor shall submit 6 copies for formal approval and distribution to relevant offices.

All drawings shall have plan and section and with sufficient details to clearly reflect the installation of the system. All material specifications shall be provided on the drawings. All information required for preparing suitable foundation, for providing suitable access to the system, for making openings in building structure, for coordination with electrical, air-conditioning and other designs etc., shall be clearly provided.

Installation shall not be allowed to commence unless approved shop drawings are in possession of the Contractor, for which purpose shop drawings shall be submitted by the Contractor to the Engineer sufficiently in advance of actual requirements to allow for ample time in checking and approval and no claim for extension of the contract time will be considered by reason of the Contractor's failure to submit the drawings on time.

Each shop drawing submitted by the Contractor shall include a certificate by the Contractor that all related conditions on site relevant to that particular installation have been checked and that no conflict exists.

Any expenses resulting from an error mistake or omission in or delay in delivery of the drawings and information mentioned above shall be borne by the Contractor.

Drawings approved shall not be departed from except on the instructions of the Engineer.

The approval by the Engineer for any submitted data, working drawings, performance curves, test certificates for any items, arrangements and/or layout shall not relieve the Contractor from any responsibility regarding the performance of the Contract. Such approval shall not also relieve the Contractor from responsibility of any error in the submitted data and workings, brought to light at any time subsequent to any approvals.

Relevant specified imported item, model cuts will be available with the authority concern for execution of work for contractor to check the models for fabrication or import.

- MATERIAL & EQUIPMENT

4.1	COLD, HOT WATER PIPES AND FITTINGS

a).	M.S./G.I. PIPES

The water supply pipes shall conform to API 5L wall B Standard ERW Sch. 40 standards. "standard specification for welded and mild steel pipe".

M.S. short pieces shall be flanged at both ends. The flanges shall conform to B.S. 4504, part 3 (PN 16). M.S. pipe pieces shall be externally protected by applying two coats of red oxides (of approved quality) and bituminous coating (grade 10/20) at the rate of 0.4 lb/Sq.ft.

b).	G.I. PIPES ONLY (wherever mentioned)

The galvanized iron pipes shall strictly conform to B.S. 1387 (medium duty) Specifications for "Steel Tubes and Tubulars suitable for screwing to B.S. 21 pipe threads" and shall be of medium grade. All screwed pipes and sockets shall conform B.S. 1740. A complete and uniform adherent coating of zinc white will be provided for galvanized iron pipes and fittings.

All screwed tubes and sockets shall have BS pipes thread in accordance with BS 21. In order to prevent damage to the leading thread, the ends of the sockets shall be chamfered internally.

A complete and uniform adherent coating of zinc will be provided for galvanized pipes.

Every tube shall be tested at the manufacturer's works to a hydraulic test pressure of 4.90 MPa (710psi) and shall be maintained at the test pressure sufficiently long for proof and inspection.

Tubes which are bundled shall be secured together by rope or soft iron or other suitable material.

The threads of all tubes shall be effectively covered with a good quality grease or other suitable compound, and each tube above 50 mm nominal bore shall have a protecting ring affixed to the un-socket screwed end.

All pipe fittings up to 75 mm dia. shall conform to BS 21 and shall be of malleable cast iron. Pipe fittings above 75 mm dia. shall be of approved material and specifications as decided by the Engineer.

c).	POLYPROPYLENE RANDOM (PPR) PIPES AND FITTINGS

Polypropylene Random Pipes and fittings shall conform to the following standard

##### DIN	  8077-8078	Resistible to all chemical elements

# DIN	16961	Smooth inner surface

##### DIN	19560	Usability for hot water all levels

##### DIN	  4279	Durable to inner pressure

DIN	16962	Conforms to connections by welding process

4.2	SOIL, WASTE, VENT & RAIN WATER DRAINAGE PIPES & PIPE FITTINGS (C. I. & uPVC)

a). C.I. PIPES

The cast iron pipe shall conform to British Standard Specifications No.416 for "Cast Iron spigot and socket soil, waste and vent pipes and fittings with spigot and socket or hubless ends. The joint shall be lead caulked or elastomeric (Rubber rings) to BS- 2494.

Cast iron pipes shall be centrifugally (SPUN) cast.

The quality of material shall be according to B.S.S. No.1452 for Grade 10.

The contractor shall supply coated pipes and fittings. The coating composition shall be of tar basis or a mixture of natural bitumen with a suitable hardener and natural asphalt. The coatings shall be smooth, tenacious, sufficiently hard, not to flow when exposed to a temperature of 63 Degrees Celsius and not so brittle at zero degrees Celsius that it chips soft when scribed lightly with the point of a pen knife.

Every pipe shall be tested at the manufacturer's work to a hydraulic test pressure of 0.07 MPa. Every pipe and fitting shall ring clearly when tested for soundness by being struck all over with a light hammer.

b).	uPVC Pipes

The material shall substantially consist of un-plasticized poly (vinyl chloride) (PVC) as per the requirements of aforesaid standard. Pipes and fittings shall be sufficiently stabilized against thermal ageing and ultraviolet (UV) light.

PIPES

- There are two types of pipes and fittings, type A and type B, as per ISO 3633 for drainage systems.  Only type B shall be used for soil, waste and venting systems.

- As per BS4514:1983, sanitary pipes and fittings shall be class “A” wall thickness 3.2mm.

FITTINGS

All fittings shall be compatible with the pipe material as recommended by the pipe manufacturer.

However, there are two types of fittings available as per ISO 3633:

      - uPVC fittings with Solvent Cement (SC) socket joint conforming to ISO 3633:1991.

      - uPVC fittings with rubber ring socket joint conforming to DIN 19560, which is compatible with ISO 3633/PS 3214.

RUBBER RINGS

The rubber rings may either be Synthetic or natural conforming to PS 1915:1987 & ISO 4633/1983 (E).

The material shall consist substantially of poly-vinyl chloride (PVC) to which may be added only those additives that are needed to facilitate the manufacture of pipes and fittings having good mechanical strength and opacity.

The pipes and fittings shall be tested mechanically and physically in accordance with the relevant Standards as and when directed by the Engineer, before and during installation.

4.4	PLUMBING FIXTURES

4.4.1 	General Requirements

Materials shall conform to the latest referenced standard specifications and other provisions stipulated herein and shall be new and unused.

All fixtures shall be imported and of the best quality and finish.

Prior to procurement of the materials, the Contractor shall be required to prepare and submit to the Engineer for his approval, a complete schedule of materials to be used in the works together with a list of the names and addresses of the manufacturers and the trade names of the materials. The schedule shall include diagrams, drawings and such other technical data as may be required by the Engineer to satisfy himself as to the suitability, durability, quality and usefulness of the material to be purchased.

Approval of the schedule shall not be construed as authorizing any deviations from the specifications unless the attention of the Engineer has been invited to the specific changes. If the material or equipment offered under this provision is, in the opinion of the Engineer, equal to or better than specified, it will be given consideration.

Plumbing fixtures shall have smooth impervious surfaces, be free from defects and concealed fouling surface. They shall be true to line, angles, curves and colour etc. Normally they shall be of local make and of the best quality available, provided.

All taps and cocks to be installed with plumbing fixtures shall be chrome plated (CP) and shall be of appropriate class to work without damage or leakage on the specified pressure of potable water system, which is 0.88 MPa (128 psi). The taps and cocks shall be of the best quality locally manufactured.

When any fixture is provided with an overflow, the waste shall be so arranged that the standing water in the fixture cannot rise in the over flow when the stopper is closed or remain in the overflow when the fixture is empty.

Plumbing fixtures shall be installed in a manner to afford easy access for cleaning. The space between the fixture and the wall shall be closely fitted and pointed so that there is no chance for dirt or vermin to collect.

When practical, all pipes from fixtures shall be run to the nearest wall. where fixture comes in contact with wall and floors, the joint shall be watertight.

Wall hung fixtures shall be rigidly supported by metal supporting members so that no strain is transmitted to the connections. Flush tanks and similar appurtenances shall be secured by approved non-corrosive screws or bolts.

Fixtures shall be set level and in proper alignment with reference to adjacent walls. No water closet shall be set closer than 400 mm from its centre to any side wall. No urinal shall be set closer than 300 mm from its centre to any side wall or partition nor closer than 600 mm centre to centre. The supply lines or fittings for every plumbing fixture shall be so installed as to prevent backflow. All cuttings, making holes etc. and making it good shall be included in the work.

Other physical/chemical properties of the fixtures are as below:

| S. No. | Physical/Chemical Properties | Pakistan Standards | European Standards |
| --- | --- | --- | --- |
| 1 | Water absorption | Less than 0.50% | Maximum 0.50% |
| 2 | Scratch Resistance | Maximum 5.5 MOH’s scale | Maximum 5 MOH’s scale |
| 3 | Resistance to Chemicals | Resistant to acids, alkalies, bases & other household cleaning chemicals | Resistant to chemicals. |
| 4 | Crazing Resistance | Crazing “NIL” | Crazing “NIL” |
| 5 | Warpage | Maximum 5.5-6mm | Maximum 6mm |
| 6 | Strength against bending | More than 700 kg/cm | 450kg/cm - 700 kg/cm |
| 7 | Thermal shock | More than 10 cycles of thermal shock from hot to cold water 15oC-200oC | More than 2 cycles of thermal shock from hot to cold water 20oC-110oC |
| 8 | Durability | Permanently durable | Durable for ever |

4.4.2 	Wash Basins

Wash basin shall be vitreous China, best quality, approved make of colour, size and type as approved by the Engineer. It shall be installed as a complete unit including C.P brass bottle trap for individual wash basin and C.P brass P trap for battery of wash basins as applicable, C.P brass strainer, heavy duty standard fixers, screws etc. approved water inlet connection pipe, stainless steel waste pipe, jointing and sealing material, etc., with all other minor accessories required to complete the job in all respect.

4.4.3 	Vanity Wash Basins

Wash basin Vanity type shall be vitreous China, best quality, approved make of colour, size and type as approved by the Engineer. Other necessary fittings shall be same as described for above Wash basin.

4.4.4 	Water Closets (European type)

European type water closet shall be wall hung, best quality approved make of colour, size and type as approved by the Engineer. It shall be installed as a complete unit including all accessories. Flush tank (13.5 liters) shall be of coupled. Trap shall be cast integral with pan. The seat shall be of smooth non-combustible non-absorbent materials like Bakulite and of the open front type fixed to the pan with hinges. The fittings shall also include approved water inlet connection pipe, nuts bolts, etc. required for complete installation.

4.4.5 	Water Closets (Orissa)

Squatting (Asian, Orissa900) type water closet shall be vitreous China, best quality local/foreign make of colour, size and type approved by the Engineer. It shall be installed as a complete unit including, approved water inlet connection pipe, low level or high level Flush tank (13.5 liters), as required. All fittings shall be installed at low level, or high level as required including interconnecting flush piping. Foot rests, P trap, jointing and sealing materials, etc. with all other minor accessories for complete installation.

4.4.6 	Kitchen Sinks

Kitchen sink shall be stainless steel or fiberglass of best quality approved make of colour, and type as approved by the Engineer, single bowl or double bowl with integral drain board of at least 1000 x 480 mm size. It shall be installed as a complete unit with arrangement for both cold and hot water supply, approved water inlet connection C.P. brass strainer, waste outlet pipe, heavy duty cast iron brackets with bolts screws etc., jointing & sealing material etc., with all other minor accessories required for complete installation.

    - Moping sink

Moping sink shall be vitreous china or fiberglass of best quality approved make of colour, and type as approved by the Engineer, best for installation in Janitor. It shall be installed as a complete unit with arrangement for cold water supply, approved water inlet connection C.P. brass strainer, waste outlet pipe, screws with bolts screws etc., jointing & sealing material etc., with all other minor accessories required for complete installation.

4.5 	MISCELLANEOUS ITEMS

4.5.1 	Taps, Cocks, showers and mixers.

All taps, cocks and mixers shall be of brass, gun metal or other equally suitable corrosion resisting alloy conforming to BS 1010 and shall be best quality approved make. The nominal size specified shall be the nominal bore of the seating. Washers for cold water cocks shall be of specially selected leather, rubber asbestos composition or other equally suitable material. Washers for hot water cocks shall be of good quality fiber, rubber - asbestos composition or other equally suitable material. Every tap, cock and mixer shall be tested, complete with its component parts, to a hydraulic pressure of at least 1.96 MPa (284.4 psi) During test it shall neither leak nor sweat.

4.5.2 	Floor traps/drains

Floor  traps/drains  shall be of cast iron or uPVC or of  other  anti-corrosive material, compatible with the material of pipe. They shall have minimum water seal of 40 mm and shall be provided with removable metal/uPVC strainers. The traps shall be of self-clearing type. The open area of the strainer shall be greater than the cross section area of the drain line to which it connects. Floor traps shall be well set in position so that there is no leakage at the joint between trap and the floor.

4.5.3 	Roof Drains

Roof drains shall be of bitumen coated cast iron compatible with the material of pipe. They shall have strainers extending at least 15 mm above the roof surface immediately adjacent to them, when installed on flat part. Bottom of strainer shall be flush with the roof surface, when installed on vertical part. Strainer shall have an available inlet area, above roof level, of not less than 1-1/2 times the area of the down-pipe to which the drain is connected.

The connection between roof and roof drain shall be made watertight by the use of proper flashing material.

4.5.4	Cleanouts

Cleanout  shall be of the same nominal size as that  of  the  pipe  on  which it is  installed. Cast Iron Cleanout  shall  consist  of tapped heavy duty cast iron ferrule  caulked  into cast iron fitting and heavy duty brass tapered even  plug. UPVC cleanout shall consist of either two 45o bends or one long radius bend both with an removable end cap and other necessary fittings/material for complete installation in floor Cleanouts shall be turned up through  floors  by  long sweep fittings, wherever the space so permits. Top  finish  of  cleanout shall be flush with  the  floor  by  means  of finished metal plate secured in  position  and  screwed firmly to the plug. Cleanout   shall  be  so  installed  that  there  is   a   clearance  of  at least 300 mm for pipes less  than  75 mm    diameter and at least 457 mm for pipes of 75 mm and larger  diameter, for the purpose of roding.

Pipe used with cleanout shall be measured and paid under pipe item. All other work of ferrule, plug, concrete work, frame and cover etc. shall be measured and paid under cleanout item.

4.5.5 	Grease Trap/interceptor

The grease trap shall be of stainless steel of specified capacity with cover, baffles and strainers to separate grease from water effectively. The grease trap shall be of approved make or equivalent and installed in the position as shown on drawings or as specified by the Engineer.

4.5.6 	Glass Mirror

The glass mirror shall be of specified size, 5 mm thick, securely fixed on hard board packing and of best quality Belgium make. The mirror shall be fixed on wall as shown on the drawing or as directed by the Engineer. All accessories required for complete fixing of mirror on wall shall be included in Contractor's scope of work.

4.5.7 	Towel Rail, Toilet Paper Holder, Soap Trays, Mirror Trays

The towel rail, toilet paper holder, soap trays & mirror trays shall be heavy duty and of best quality All accessories for complete installation of towel rail, toilet paper holder, soap tray and mirror tray shall be included in the Contractor's scope of work.

4.5.8 	Gully Trap

Gully trap shall be of cast iron with specified size outlet. The inlet shall be provided with cast iron, medium duty grating. The open area of the grating shall be at least 1-1/2 times the area of the outlet. The trap shall be of P-Type with a minimum water seal of 50 mm. It shall be installed as a complete unit including all civil works as shown on relevant details and drawings.

4.5.9	Cast Iron Grating

Cast iron grating shall be of the specified size. The specified size shall mean the clear span. Cast iron grating shall be complete with frame. They shall be of Light/medium duty type to resist normal traffic loads, the casting shall be sound and free from all defects. The frame shall be set in place at the time of pouring of concrete. Openings in grating shall be in approved pattern.

    - Water Disinfection System

The system shall comprise of Ultra-Violet (U/V) tubes of best quality foreign make installed and fitted in a standard cabinet with all other accessories. The flow rate shall be 250 gallons/ hour. The pressure available at the inlet to the system shall not be more than 5psi. The unit shall have control/gate valves and the cabinet shall have a locking arrangement.

    - Water Filtration System

Water filtration system shall be installed as shown on drawings. They shall be of best quality local/foreign make. Each filter shall have a crystal housing of a durable material. The flow rate shall be 2 to 6 gpm with a maximum pressure of 70psi and a temperature of 35oF to 100oF.

Stage 1:- 	Stage 1 shall use a “poly propylene Yarn In depth Sediment filter cartridge”, for removal of dust, rust, silt, scale and unseen suspended particles. It shall have a filtration rating of 5-micron.

Stage 2:- 	In this stage a “Granular Activated Carbon (GAC) cartridge” equipped with a post-filter of 1-micron is recommended, for removal of chemicals and unpleasant taste and odor.

Stage 3:- 	This stage must provide 30,000 MW.sec/sq.cm energy to guarantee 100% sterilization and ensure effective control of microbiological contamination.

Other specifications of water filtration system shall be as per manufacturer’s recommendations. The Contractor shall submit a detailed report and quotation of the manufacturer to the Engineer for final approval. The report/quotation shall clearly identify specifications as per requirements of the project.

- EXECUTION

5.1	GENERAL

The Contractor shall be responsible for his work until its completion and final acceptance, and shall replace any of those that may be damaged, lost or stolen without any additional cost.

All openings left in floor for passage of lines of water supply, soil, waste, vent, etc. shall be covered and protected.

All open ends of pipes shall be properly plugged to prevent any foreign material from entering the pipe. Misuse of plumbing fixtures to be installed under this Contract is prohibited during the currency of the contract.

All metal fixture trimmings shall be thoroughly covered with non-corrosive grease which shall be maintained until all work is completed.

Upon the completion of work, all fixtures and trimmings shall be thoroughly cleaned, polished and left in first class condition.

Before erection, all pipes, valves, fittings, etc. shall be thoroughly cleaned of oil, grease or other material.

All special tools for proper operation and maintenance of the equipment provided under this Contract shall be delivered at no additional cost.

The Contractor shall allow in his bid for cost of all cutting, making holes and subsequent making it good to the desired finish as per approval of the Engineer. No separate payment shall be made for this item.

The Contractor shall allow in his bid for the cost of providing protective painting or coating as specified in the relevant sections and no claim shall be entertained for this item.

All pipes shall be properly installed as shown on the drawings and/or as directed by the Engineer, and shall be as straight as possible forming right angles and parallel lines with the walls and other pipelines. The position, gradients, alignment and inverts shall be as shown on the drawings and/or as directed in writing and set out by the Engineer.

The arrangement, positions and connections of pipe fittings and appurtenances shall be as shown on the drawings. The Engineer reserves the right to change the location etc. Special precautions shall be taken for the installation of concealed pipes as shown on the drawings and/or as required. Should it be necessary to correct piping so installed, the Contractor shall be held liable for any injury caused to other works in the correction of piping. The Contractor shall closely coordinate with other works during the entire stage of execution.

A minimum distance between different services shall be maintained as shown on the Drawings and/or as approved by the Engineer.

Pipes should be installed in such a manner that minimum distance should always be maintained between pipe and wall, beams, columns, etc. Pipes shall be supported on hangers and brackets as shown on the drawings or as directed by the Engineer.

Waste-water outlet from each fixture shall be individually trapped. Each vent terminal shall extend to the outer air and be so installed as to minimize the possibilities of clogging and the return of foul air to the building.

When the roughing-in is completed, the plumbing system shall be subjected to test prior to concealing the roughing-in, in order to ascertain that all threads and connections are watertight.

Cast iron soil and drainage fittings for change in direction shall be used as follows:-

*Vertical to horizontal : short sweep or long-turn for diameter 75 mm and larger; long sweep or extra-long-turn for less than 75 mm. dia.

*Horizontal to vertical : quarter bend or short turn.

All fittings with hubs shall be aligned so that the hub faces upstream. No drainage or vent piping shall be drilled.

All exterior openings provided for the passage of piping shall be properly sealed with snugly fitting collars of metal or other approved rodent-proof material securely fastened into place.

Joints at the roof, around vent pipes, shall be made water-tight by the use of lead, copper, galvanized iron, or other approved flashing or flashing material. Exterior wall openings shall be made watertight.

Each length of pipe & each pipe fitting, trap, fixture, & device used in a plumbing system shall have cast, stamped or indelibly marked on it the maker's mark or name, the weight, type & classes of the product, when such marking is required by the approved standard that applies.

Where different sizes of pipes, or pipes and fittings are to be connected, the proper size increasers or reducers or reduced fittings shall be used between the two sizes.

Any fitting or connection which has an enlargement, chamber, or recess with a ledge, shoulder, or reduction of pipe area that offers an obstruction to flow through the drain pipe is prohibited. The vertical distance form the fixture outlet to the trap weir shall not exceed 600 mm. Each fixture trap shall have a water seal of not less than 50 mm and not more than 100 mm.

Full S, bell, crown vented traps and traps/depending for their seal upon the action of movable parts are prohibited. No fixture shall be double trapped. Where fixture comes in contact with wall and floors, the joint shall be water-tight. Piping in ground shall be laid on a firm bed for its entire length.

Piping in the plumbing system shall be installed without undue strains and stresses. Vertical piping shall be securely held to keep the pipe in alignment and carry the weight of the pipe and contents. Horizontal piping shall be supported to keep it in alignment and prevent sagging. Hangers and anchors shall be of metal of sufficient strength to maintain their proportional share of pipe alignments and prevent rattling. Hangers and anchors shall be securely attached to the building under construction. It must be clearly understood that the Contractor shall be fully responsible for hangers and supports and shall obtain prior approval of design as to the shape, material, dimensions, spacing etc.

Piping in concrete or masonry walls or footings shall be placed or installed in sleeves which will permit access to the piping for repair or replacement.

5.2	COLD, HOT WATER PIPES AND FITTINGS

The run and arrangement of all pipes shall be as shown on the Drawings and as directed during installation. All vertical pipes shall be erected plumb and shall be parallel to wall and other pipes. All horizontal runs of piping shall be kept close to walls. If required to change the location etc. during the currency of the work, the Contractor will do so at no additional cost. Screwed joints in G.I. pipes and welded joints in M.S. pipes shall be made perfectly tight, without the use of any filler except approved jointing compound or tape. Wherever required to make flanged joints, they shall conform to BS 10 Table D.

Furnish and install all pipe passing through floors and walls with sleeves of G.I. sheet, 18 gauge, the inside dia. of which shall be at least 1/2" greater than the outside dia of the pipe passing through it. Sleeves in exterior walls and pits shall have anchor flanges and space between pipe and sleeve shall be caulked and sealed watertight. At waterproof locations, an approved water-proof type pipe sleeve shall be provided.

All embedded water supply piping shall be wrapped with approved anti-corrosion polyethylene tape. All exposed piping shall be painted with two coats of enamel paint over a coat of red oxide.

All exposed pipes running in ducts shall be wrapped with thermal insulation as specified below.

##### a).	Thermal Insulation

All cold & hot water, fire water and hot water return piping shall be insulated as specified herein. Prior to insulation the pipes shall be hydraulically tested and cleaned.

Nominal Pipe 		Thickness of

Dia. (mm)		 insulation. (mm)

15 (1/2") 			 25

20 (3/4") 		 	 25

25 ( 1" ) 			 25

32 (1-1/4") 			 25

40 (1-1/2") 			 25

50 ( 2" ) 		 	 25

65 (2-1/2") 			 25

75 ( 3" ) 		 	 25

Insulation shall consist of pre-formed fiberglass pipe insulation, with factory applied reinforced aluminum vapor barrier, single layer in semi-circular halves, consisting of long, fine glass fibers, bonded with a temperature resistant binder, free from shot or coarse fibers, damage resistant, light in weight, easy to handle, cut and fit. The product shall comply with the requirements of B.S. 3958: Part 4. The insulation shall be rot-proof, odorless, non-hygroscopic, and shall not sustain vermin. The fiberglass insulation shall be covered with a layer of approved polyethylene tape in the field. Further reinforcement shall be provided by the use of 20 mm wide soft aluminum bands, generally spaced at 457 mm and on either side of elbows and tees. All butt joints shall be sealed with self-adhesive type of approved quality adhesive tape.

All trimmed sections shall be secured by wrapping of approved type of self adhesive tape to form a complete waterproof seal. All work shall be done in a neat and workmanlike manner, and should reflect recommended practice.

All Hot water and Hot water return lines concealed in walls only, shall be provided with Glass wool blanket insulation.

b).	Pipe work Supports

Pipe work supports shall be installed in order to allow free movement due to expansions and contraction. Supports shall be arranged adjacent to joints, changes of direction and branches. Each support shall carry the overall weight of pipe work and water to be borne by it. The intervals between pipe supports shall not exceed the following or as specified by the manufacturer, whichever is minimum.

Maximum interval between supports (metres)

-------------------------------------------------------------------------------------------------------

Steel pipes

Nominal

Dia mm 		   	        Horizontal 	                      Vertical

-------------------------------------------------------------------------------------------------------

10 				1.7 			1.7

15 				2.0 			2.0

20 				2.4 			2.4

25 				2.7 			2.7

32 				2.7 			2.7

40 				3.0 			3.5

50 				3.4 			3.9

65 				3.7 			4.3

80 				3.7 			4.3

100 				4.1 			4.6

125 				4.4 			4.9

150 				4.8 			5.4

200 				5.0 			6.0

-------------------------------------------------------------------------------------------------------

Single pipes hung from floor slabs shall be supported on rod hangers. Where two or more pipes are involved a channel or angle from shall be fitted to the underside of slab by two hangers and the pipes shall be supported from the channel iron by rod hangers and flat iron hands.

All hanger rods shall have double nuts and beveled washers to allow the hanger rod to swing.

Multiple pipe runs along walls shall be supported on purpose made substantial angle and channel frames securely fixed to the wall, floor and ceiling as necessary. All pipes shall be arranged to slide on the steel supports and U-bolts shall be provided to form a rigid guide.

Exposed pipe work shall be supported on channel, angle iron or with U-bolts to form a rigid guide.

All U-bolts, except used as anchors, shall have a pair of nut and washers on each leg with the supporting steel flange clamped tight between the pair of nuts to form a rigid guide and allowing the pipe to slide axially,. U- bolts shall be provided on alternate pipe bracket.

Small pipe work running along skirting shall be supported by standard built-in or screw-on type clips.

Pipes shall be individually supported. Pipes shall not hung from other pipes.

Points at which pipes pass through walls, floors, connections to plant, equipment and heat emitters, etc. do not constitute points of supports for the pipes.

Vertical pipes shall be supported at the base or at anchor points to withstand the total weight of the riser. Brackets from risers shall not be used as a means-of support for the riser.

Vibration isolators to be provided with the hangers as approved by the Engineer.

5.3	POLYPROPYLENE RANDOM PIPES & Jointing

5.3.1	Jointing Techniques

The surfaces of the pipes and fittings must be clean and without impurities. Pipe ends must be clean, cut at right angles. It is recommended to cut 1cm from the pipe ends in order to prevent possible micro-cracking due to incautious handling.

Before carrying out the welding, check that the poly-fusion device operates correctly and that it reaches the required welding temperature (260oC + 5).

Jointing is done by heat fusion (welding) by means of welding machine.  Welding is carried out by means of heating simultaneously the male and female parts to be joined together, once the welding temperature is reached the joint is made and held for cooling time.  (see table I  below )

    - Welding Instructions using socket welding machine

- Check whether the welding tool corresponds to the size you need to join.

- The welding tool/device has reached the necessary operating temperature of 260oC +	10

- Cut the pipe at right angles to the pipe axis by using cutter or a hack saw.

- Clean the pipe from burrs, cutting and chips

- Mark the welding depths at the end or pipe

- Push the end of pipe up to the marked welding depths in the welding tool, at the same time push the fitting, into the welding tool.

- After the stipulated heating time quickly remove pipe and fitting from the welding tools and join them immediately, forcing the pipe into the fitting until the marked welding depth is covered by the bead of Polypropylene from the fitting

- The joint elements have to be fixed and aligned within the specified assembly time.

- After the cooling time the fused joint is ready for use.

The heating time starts when pipe and fitting have been pushed to the correct welding depth in the welding tool

| Est. Diameter (mm) | Welding Depth (mm) | Heating Time DVS 2207 * (sc). |  | Heating time (sc.) | Cooling Time (min.) |
| --- | --- | --- | --- | --- | --- |
| 20 | 14.0 | 5 | 8 | 4 | 2 |
| 25 | 15.0 | 7 | 11 | 4 | 2 |
| 32 | 16.5 | 8 | 12 | 6 | 4 |
| 40 | 18.0 | 12 | 18 | 6 | 4 |
| 50 | 20.0 | 18 | 27 | 6 | 4 |
| 63 | 24.0 | 24 | 36 | 8 | 6 |

The heating time have to be increased 50% if average temperature is under + 5oC

    - Welding of PPR Pipes

- Cutting of pipe at right angle with a cutter.

- Marking of welding depth on the pipe end.

- Simultaneous heating of both pipe and fittings according to required heating time (as per given data).

- Pushing of pipe end into the fitting and alignment of the assembly within specified time period

- Finish joint.

    - Installation Principles

      - Fastening technique for open installation

The selection of fastening material and its application have to be determined as:-

- Fixed Point

- Sliding Point

Pipe clamps are such as to meet all requirements and ensure that no mechanical damage on the pipe surface can occur.

      - Fixed Point

Valves and connections resisting to bending stresses have to be fastened by means of points.  In particular cases the fixed points are to be positioned closed to branches or wall passages.  The axial expansion will be compensated between two points.  The assess the resistance of the fixed points one has to take into account the stresses to which they will be subjected, caused by linear expansion, weight of the piping and weight of the transportation fluid. Fixed points should be delimited on both sides of the clamp, availing oneself of the rim fittings or valves.

      - Sliding Point

The sliding points must keep the system aligned and support it, and allow the axial sliding of the piping as well.  The sliding are to be firmly mounted in order to prevent vibration and transmission of noise.

Distance between the support points in cm.

| ## Pipe diameter | Temperature in oC |  |  |
| --- | --- | --- | --- |
|  | 20 | 50 | 80 |
| 20mm | 85 | 70 | 60 |
| 25mm | 85 | 80 | 70 |
| 32mm | 100 | 85 | 85 |
| 40mm | 110 | 100 | 90 |
| 50mm | 125 | 110 | 90 |
| 65mm | 140 | 125 | 105 |

5.4	SOIL, WASTE, VENT & RAIN WATER DRAINAGE PIPES & PIPE FITTINGS (C. I. & uPVC)

All cast iron soil pipes and fittings shall be installed to the lines and grades shown on the drawings or as directed by the Engineer. When required to be installed above ground floor level, suitable and substantial number of hangers and supports of approved type and make shall be provided. No piping shall be hung from the piping of other systems. Clamps shall be provided on not more than 1.5 meter centres or a minimum of one hanger per each length of pipe whichever is smaller. Where excessive numbers of fittings are installed, additional clamps will be provided.

All exposed C.I. soil, waste and vent pipes shall be given two coats of synthetic enamel paint. Materials for painting shall be high quality product of well-known manufacturer and will be approved by the Engineer before using. The instructions of the manufacturer regarding all painting work shall strictly be adhered to Pipes passing through walls, floors, etc. shall be provided with sleeves of approved design. All vent pipes to be installed in the system shall be provided with approved cowl and will rise at least 0.70 meter above the roof.

Caulked joints for cast iron bell-and-spigot soil pipe shall be firmly packed with oakum or kemp and filled with molten lead not less than 22 mm deep and not to extend more than 3 mm below the rim of the hub. Rubber ring joints shall also be allowed. No paint, varnish, or other coatings shall be permitted on the jointing material unit after the joint has been tested and approved

Pipes passing through walls, floors, etc. shall be provided with sleeves of approved design. All vent pipe to the installed in the system shall be provided with approved cowl and will rise at least 0.70 meter above the roof.

Special requirements for uPVC pipes and fittings area as under:

Maximum Interval between Supports (m)

(Support centers for uPVC pipe work systems)*

### Nominal					PIPEWORKS

| Diameter, de | Horizontal (10xde) | Vertical |
| --- | --- | --- |
| (mm) | (m) | (m) |
| 40 | 0.40 | 1.2 |
| 50 | 0.50 | 1.5 |
| 75 | 0.75 | 2.0 |
| 110 | 1.10 | 2.0 |

* The values shown are for general installations only. Attention is drawn to special requirements that may be needed in more demanding applications.

All steel clamps, hangers, supports etc. shall be given one coat of red oxide primer and two coats of synthetic enamel paint.

All exposed uPVC pipes shall be given two coats of approved colour water based emulsion paint (note that oil based paints must be avoided.

PRECAUTIONS

Following points describe how an uPVC must be cared of while concreting it:

- The depth of concrete cover above uPVC pipe depends on the pipe gradient. However, a minimum of 1 (one) inch concrete cover must be provided.

- When using cemented joints, the adhesive should be given sufficient opportunity to harden before the pipe is concreted in.

- Horizontal lines that are concreted-in should be anchored against upward movement and should be adequately secured while the concrete is being poured.

- During the pouring and setting of concrete, necessary care shall be taken to prevent physical damage to the pipes.

- When using heated concrete or when steaming the concrete, the sensitivity of uPVC material to temperature changes should be borne in mind.

- Concrete mortar that is used before concreting-in shall include no sharp-edged material.

- Avoid excessive misalignment of the pipes.

- Avoid excessive tightness of joints.

- Provide sufficient expansion joints to allow thermal movement or regression.

- Use only allowed cleaning & descaling techniques for different situations & locations (as described in ISO/TR 7024-1985E) when a pipeline gets choked or blocked.

DELIVERY CONDITIONS

The internal and external surfaces of pipes and fittings shall be smooth and free from grooving, blistering and any other surface defect. The materials shall not contain visible impurities or pores. Pipe ends shall be cleanly cut, and the ends of pipes and fittings shall be square with the axis of the pipe

MARKINGS

Pipes, fittings and sealing rings shall be marked clearly and indelibly so that legibility is maintained for the life of products under normal conditions of storage, weather and use.

The markings may be integral with the product or on a label. The markings shall not damage the product.

###### PIPES

Pipes shall be marked with at least the following information:

- Manufacturer’s name or trade mark;

- Pipe material;

- Nominal diameter of pipe;

- Nominal wall thickness of pipe

- Manufacturing information, in plain text or in code, providing tractability of the production period to within the year and month and the production site if the manufacturer is producing at several national or international sites.

- The number of this International Standard.

Pipes with a nominal laying length up to and including z2 meters shall be marked with at least once. Pipes with a nominal laying length greater than z2 meters shall be marked at intervals of z3 meters at the most. The values of z2 and z3 shall be as specified by the authorities in each country.

###### Fittings

Fittings shall be marked with at least the following information:

###### Manufacturer’s name or trade mark;

###### Fitting material (may be given on packing only in the case of PVC, provided this information is not required on each article by national authorities);

###### Nominal diameter of fitting;

###### Classification (where applicable)

###### Values of angles, if any;

###### Manufacturing information, in plain text or in code, providing tractability of the production period to within the year and month and the production site if the manufacturer is producing at several national or international sites (may be given on packing only, provided this information is not required on each article by national authorities);

###### The number of this International Standard (may be given on packing only, provided this information is not required on each article by national authorities).

###### Sealing Rings

Sealing rings shall be marked with at least the following information:

- Manufacturer’s name or trade mark;

- Nominal diameter of ring;

- Manufacturing information, in plain text or in code, providing traceability of the production period to within the year and month and the production site if the manufacturer is producing at several national or international sites.

6.	TESTING AND COMMISSIONING

6.1	COLD AND HOT WATER PIPES

All water distribution system shall be tested whole or in part to 2 times the working pressure with a minimum test pressure of 200psi. The contractor shall pay for all device, materials, supplies, labor and power required for the test. The test will be run for two hours at the specified pressure and there should be no leakage in the system. Defects revealed by the test shall be repaired and the whole test rerun until the system proves to be satisfactory.

After all the pipes and fixtures have been properly laid and tested, they shall be flushed clean with water and then disinfected with water solution of chlorine of at least 50 ppm strength for a contact period of 6 hours. The system will be finally flushed with clean water.

6.2	SOIL, WASTE, VENT & RAIN WATER DRAINAGE PIPES & PIPE FITTINGS (C. I. & uPVC)

The entire system of drains, waste, and vent piping inside the building shall be tested by this Contractor under a water test. Every portion of the system shall be tested to a hydrostatic pressure equivalent to at least 3-meter head of water. After filling this Contractor shall shut off water supply and shall allow it to stand two hours, under test during which time there shall be no loss or leakage.

The Contractor shall furnish and pay for all devices, materials, supplies, labor and power required in connection with all tests. All tests shall be made in the presence of and to the satisfaction of the Engineer.

The Contractor shall also be responsible for the repair of this work & other trades work that may be damaged or disturbed by the tests. Defects disclosed by the tests repaired. Work shall be replaced with new work without extra cost to the Employer. Tests shall be repeated as directed, until all work is proven satisfactory.

All fixtures shall be tested for soundness, stability, support and satisfactory operation.

7. 	MEASUREMENT AND PAYMENT

7.1 	COLD & HOT WATER PIPES & FITTINGS

7.1.1 	Measurement

Measurement for acceptably completed works of supply and installation of cold and hot water pipes shall be in running feet length.

No measurement shall be made for earthworks, pipe fittings, jointing, hangers, clamps, brackets, sleeves, insulation, cutting and breaking concrete and then making it good, applying protective painting, coating, cleaning, testing and disinfecting etc. and the measurement will be for the full work specified herein. All these works will be included in running feet of specified pipe size in BOQ.

7.1.2 	Payment

Payment for acceptable measured quantity will be made at the unit rate per running feet length of cold and hot water pipes quoted in the Bill of Quantities. The amount bid shall be the full payment for completion of the work in all respects as specified herein.

7.2 	uPVC and C.I. SOIL, WASTE & VENT PIPES

7.2.1 	Measurement

Measurement for acceptably completed works of supply and installation of uPVC & C.I. pipes, will be in running feet length and the work to be done shall include all pipe fittings, jointing, hangers, clamps, brackets, sleeves, cutting and breaking concrete and then making it good, applying protective painting, coating, cleaning and testing.

7.2.2 	Payment

Payment will be made at the unit rate of bid per running feet length of pipe acceptably supplied and installed. The amount bid shall be full payment for the work specified herein.

7.3 	PLUMBING FIXTURES

7.3.1 	Measurement

Measurement for plumbing fixtures will be made as per actual number acceptably installed. The Contractor's bid against these items shall include installation of complete unit as specified herein, inclusive of all work from inlet connection of water supply to outlet connection with the sanitary system, complete as per Contract Documents and/or as directed by the Engineer.

7.3.2 	Payment

Payment for plumbing fixtures shall be made at the applicable unit price per number bid for the respective item in the Bill of Quantities. The amount bid shall be full payment for the work specified herein.

7.4 	MISCELLANEOUS ITEMS

7.4.1 	Measurement

Measurement for acceptably completed works of floor drains, roof drains, cleanouts, glass mirror, towel rail, toilet paper holder, soap trays, mirror trays, cold and hot water mixers, tee-stop cocks etc. shall be made on the basis of actual number acceptably installed in position. The Contractor's bid against these items shall include installation complete as specified herein and/or as shown on the Drawings.

7.4.2 	Payment

Payment for acceptably measured quantity of floor drains, roof drains, cleanouts, glass mirror, towel rail, toilet paper holder, soap trays, mirror trays, cold and hot water mixers, tee-stop cocks etc. shall be made at the applicable unit rate per number quoted in the Bill of Quantities. The bid amount shall be full payment for the works specified herein and as shown on the Drawings.