SECTION - 8001

GENERAL SPECIFICATIONS FOR ELECTRICAL WORKS

1.0	SCOPE

The works related to the electrical & communication systems, which are included in the scope of this Contract, are shown on the Drawings, stated in the Specifications and Bill   of Quantities and explained in these specifications. The works shall broadly include but not limited to the following:

-    	Power Transformers

-    	HT Switchboards

- LT Switchboards

-	LT Distribution Boards

- HT & LT Cables / Distribution

- Wiring Accessories

-	Internal / External illumination

-	Earthing

-	Lightning Protection

- Structured Cabling

- Fire Alarm System

- Motor Control Centers

The Contractor shall also be responsible to supply any other equipment not specifically mentioned in these Documents but which is necessary for proper operation of the system as intended in the scope of this Contract. The Contractor shall solely be responsible for ensuring proper functional requirements of various equipments and shall be responsible for furnishing any additional piece of   equipment and for making modification in the equipment as desired and/or approved by the Engineer to achieve proper co-ordination with various equipment offered in the bid and also with those installed by others.

2.0 	RULES & REGULATIONS

The entire electrical installation/work shall be carried out by licensed Contractor, authorized to undertake such work under the provisions of the Electricity Act 1910 and The Electricity Rules 1937 as adopted and modified upto date by the Government of Pakistan.

All works shall be carried out in accordance with the latest edition of the Regulations of the Electrical Equipment of Buildings issued by the Institute of Electrical Engineers-London, the Contract Documents, The Electricity Rules 1937 and bye-laws that are in force from time to time. Any discrepancy between these Specifications and any other rules and regulations shall be brought to the notice of Engineer for his instructions and the decision of the Engineer shall be final and conclusive.

The Contractor shall be responsible for completing all formalities and submitting the test certificates as per prevailing rules and regulations, and shall have the installation passed by the Government Electric Inspector of that region. All requirements of the Electric Inspector and the electric supply company shall be complied with.

3.0	AMBIENT CONDITIONS

All material and equipment supplied and installed shall be designed, manufactured and tested to meet the following ambient conditions unless specifically stated otherwise for any material/equipment.

Maximum indoor ambient temperature   	:	24     	Degree Celcius

Minimum indoor ambient temperature    	:  	Zero  	Degree Celcius

Maximum outdoor ambient temperature  	:	45     	Degree Celcius

Minimum outdoor ambient temperature   	:	3	Degree Celcius

Maximum Relative humidity          	    	:	90	Percent

Maximum Altitude of project          		:	1150	feet above the

mean sea level.

4.0	STANDARDS

The latest standards, codes and recommendations of reputable institutions shall be applicable for the material and equipment specified herein and for installation work. Such institutions to be BSS, VDE, IEC, NFPA etc. In case the Specifications laid down herein differ from those given in the standards, then the equivalent or better specifications shall govern. Wherever applicable the equipment shall also conform to the requirements of Pakistan Standard Institution (PSI).

Contractor shall maintain at the site office one copy of the standards/codes/ recommendations as applicable to the works and will furnish the same as and when required by the Engineer / Employer.

5.0	SYSTEM DATA

Unless otherwise specified elsewhere, all equipment and material shall be designed to operate satisfactorily with the following minimum requirements without any de-rating.

a)   	Voltage rating of equipment 	: 	HT:  11 kV, 3 phase + 10%

LT: 400 V,   3 phase + 10%

230 V,  1 phase + 10%

b)   	Frequency                            	:  	50 Hz + 2 Hz

In general, the electrical colour coding of switchgear cubicles, control panels, desks etc., shall be in accordance with the respective IEC Recommendations.

Live parts of electrical connections shall be colour coded according to IEC 446 as follows:

Conductor     		Coding			Colour

Designation              	Alphanumeric

A.C. Network	Phase 1	  	    L 1                    		   red

Phase 2	  	    L 2                		   yellow

Phase 3	  	    L 3                    		   blue

Neutral      		    N                			   black

D.C. Network 	Positive     		    L+            			   white

Negative     		    L-            			   black

Earthing         	Protective Earth	    PE     			   green/yellow

Earth        		    E				   green/yellow

Control Cables

The Control Cables shall be manufactured according to specifications for L.T. Cables. The Control Cables shall be of multi-core, PVC insulated type withstanding without deterioration the conditions prevailing at the place of installation. The cross section of cable shall be as per the requirement of the system.

All the cores should be numbered and/or colour coded or otherwise properly identified. At-least 20% spare cores shall be provided in all Control Cables.

No separate payment is admissible for supplying, installing, testing and commissioning of control cables and is deemed to have been included in the BOQ rates of the respective equipment.

Distance in between power, communication and control cables shall be kept as per requirements laid down by NEC800, NFPA 70 and EN50174-2.

6.0	EQUIPMENT

6.1	IP Degree of Protection

The equipment shall have IP degree of protection as follows, unless mentioned other wise :

-	IP 42 for indoor areas

-	IP 54 for indoor damp areas and shaded/covered areas

-	IP 65 for open outdoor areas

If properly rated equipment is not available, the Contractor shall provide field enclosures to attain the required IP degree of protection. If necessary cooling/exhaust fans and / or anti condensate heaters shall also be provided. No separate payment shall be made to attain the required IP degree of protection.

6.2	Identification & Labeling

All devices, meters cabling, wiring and auxiliaries shall be properly labeled for identification.  Labeling of equipment shall be done by means of flameproof material using indelible ink/marking. The labeling shall be such as to ensure uniformity and shall facilitate study of control diagrams/ drawings during operation and maintenance.

All labeling shall be of suitable size to be visible from the operating conditions/positions at site.

6.3	Lamp Test Facility

All equipment / switchboards, etc. shall be provided with common lamp test facility.

7.0 	SHOP DRAWINGS AND DATA TO BE FURNISHED BY THE CONTRACTOR

The shop drawings and/or technical data to be furnished by the Contractor for each electrical equipment shall include, but not limited to the following:

(a) 	Structural drawings showing foundations, RCC details dimensional plans, elevation and sections on a suitable scale.

(b) 	Electrical drawings showing:

-	Line diagrams of switchboards, distribution boards, and motor control centers with detailed wiring diagrams, elevations/internal component layout and other standard details.

-	Complete shop drawings with necessary execution details such as no. of wires, size of conduit, etc.

(c) 	Technical literature and manufacturer's characteristic data with the description of materials and weights of all equipment as instructed by the Engineer.

At least three (3) copies of the shop drawings and/or technical data of the equipment shall be submitted to the Engineer for checking and approval.

8.0	MANUFACTURER'S INSTRUCTIONS

The Contractor shall supply to the Engineer in properly bound form six   (6) copies of manufacturer's instruction manuals for installation, testing, commissioning, operation and maintenance of the specified equipment including manuals of spare parts and tools of the equipment. At least two copies of the documents shall be submitted in original.  The installation instructions shall be submitted 2 weeks prior to commencement of installation of each equipment, and operation and maintenance instruction at the time of commissioning. If the Contractor fails to provide the documents the Engineer shall withhold issuance of requisite certificates and deduct suitable amount from the payments to the Contractor.

- 9.0	GUARANTEE

- The Contractor shall furnish written guarantee of the manufacturer or supplier with   respect to satisfactory performance of each equipment. Guarantee shall be given for replacement and repair of part or whole of the equipment, which may be found defective in material or workmanship. The guarantee shall cover the duration of Defects Liability Period as defined in the Conditions of Contract. This guarantee  shall not relieve the Contractor of his obligations  and he will be fully  responsible  for  the  repair  or  replacement  of   any defective  material  in  time,  so as not to cause  any  undue  delay  in carrying out the repairs and/or replacements.

- 10.0	Danger Boards with Signs, Designation and Shock / First Aid Charts and Fire Fighting Equipment

- Danger Boards having signs and designation of the room shall be installed on the external door of HT, LT, Power transformer and Low Voltage DG Set Rooms. Shock/First Aid Charts shall be installed in H.T, L.T and Low Voltage DG Set Rooms.

- Potable fire fighting extinguisher suitable to control electrical fire shall be provided in HT, LT, Power transformer and Low Voltage DG Set Rooms.

- All the above items shall also be provided, wherever required to comply the requirements of the Pakistan Electricity Rules/Electric Inspector.

- Laminated single line and adequate detail drawings on proper boards highlighting the main system features shall be displayed/ fixed in respective electrical and communication rooms.

11.0	ASSOCIATED CIVIL WORKS

- Except  where   separately stated in the Bill of Quantities the cost  of  all civil  works  associated with any BOQ item of electrical works,  such  as excavation  and backfilling of earth, compaction of the earth,  foundation pads, thrust boring, chiseling, making openings, etc. shall deemed to be included  in  the  price quoted  against  respective  items. No separate payment for such works will be made.  Such works will also include repair of any damage to civil works caused by the Contractor during electrical installation.

- 12.0	INSTALLATION INSTRUCTIONS - GENERAL

- The  Contractor shall furnish all labour, materials, tools  and  equipment required   to install, connect, test and commission all electrical equipment specified herein, whether or not such equipment is furnished by him or by others.

- For all equipment to be installed by the Contractor, the Contractor shall supply and install all erection materials such as foundation bolts, washers, nuts, etc. as required and without any additional costs.

- The Contractor shall set out the works himself as per Specifications and Drawings and shall properly position the equipment on specified foundation/location. In  general,  the  manufacturer's  instructions for installation   shall  be followed. Any defect or faulty operation of equipment due to the  Contractor  not  following  the  manufacturer's instructions shall be corrected and repaired by the Contractor at his own cost.

- For any deviation from the working drawings that are deemed  necessary by  the Contractor due to site conditions, he shall submit  the  details and obtain the Engineer approval before starting such works.

- 13.0	FACTORY TESTS

- All type and routine tests on Low Voltage D.G. set, Power transformers, HT switchboard, LT switchboard, LT distribution boards, Motor Control Center, High tension cables, Low tension cables and all other equipment shall be performed at the manufacturer's   works in the presence of the Engineer and the Employer or their representative. Type tests may be waived off in case test certificates  are submitted  as  certified by an Engineer approved  standard  laboratory of international repute; but merely producing the type test certificates will not relieve the manufacturer to carry out the required  standard/routine tests.

- The Contractor shall inform the Engineer about the date and time of test of each equipment at least two weeks in advance. This shall, however, be done after the Contractor has got the test procedures duly approved by the Engineer. The witnessing of test by the Engineer and the Employer shall not absolve the Contractor from his responsibility for the proper functioning of the equipment, and for furnishing   the guarantees referred to in clause 9.0. All test results shall be supplied in quadruplicate. All expenses for carrying out the tests as the expenses for the Engineer and the Employer to witness it shall be borne by the Contractor and deemed to have been included in the tender bid. Provision for at least two person’s visit for Factory Acceptance Tests shall be made to include one representative each from the Employer and the Consultant/Engineer. The contractor shall undertake all formalities as may be required for the Engineer or his representative to enable him make the visit.

- 14.0 	TESTING - GENERAL

- 14.1 	Scope

- Upon completion of the installation, the Contractor shall perform field tests on all equipment, cables, materials and systems. All tests shall be conducted in the presence of the Engineer or his representative for the purpose of demonstrating equipment  or system compliance  with Specifications. The  Contractor shall submit for Engineer's approval complete details of tests to be performed describing the procedure,  test  observations  and expected results.

- The Contractor shall furnish  all  tools,  instruments,  test   equipment, materials,  etc.,  and  all  qualified  personnel  required  for  the  testing, setting and adjustment of all electrical equipment and material  including putting the same into operation.

- All  tests  shall  be  made with proper regard  for  the  protection  of  the personnel and equipment and the Contractor shall be  responsible  for adequate  protection  of  all personnel and equipment  during  such  tests.  The cost of any damages or rectification work due to any accident during the tests shall be the sole responsibility of Contractor.

- The Contractor shall record all test values of the tests made by him on all  equipment. Four (4) copies of all test data and results certified by the  Engineer shall be given to the Engineer for record purposes. These shall also include details of testing method, testing equipment, diagrams, etc.

- The   witnessing  of  any  tests  by  the  Engineer  does  not  relieve   the  Contractor of his guarantees for materials, equipment and  workmanship, or as any other obligations of Contract.

- 14.2	Low Voltage D.G. Sets

- Prior to the tests, the contractor shall submit manufacturer’s recommended detailed description of the test procedures to be conducted for  Engineer’s approval.

- The Contractor shall carry out full site load and no load tests in accordance with IEC, ISO or BS Specifications for site commissioning. The inspection and tests shall include but not be limited to:

- Basic Tests:			Insulation Resistance

- Earth Continuity

- Earth Loop Impedance

- Polarity

- Phase Rotation

- Voltage and Frequency

- Starting System

- Protection Equipment

- Synchronizing System

- Load Sharing System

- Battery:			Nominal Voltage

- Discharge Voltage

- Specific Gravity of Electrolyte

- Level of Electrolyte

- Charging System

- Lubrication:			Check as required by manufacturer

- Operational Check at 		Oil Pressure

- Start-up			Fuel Oil Leaks

- Operation of Safety Devices

- Operational Speed

- Automatic Control

- Instrument Check

- Exhaust Check

- Undue Vibration

- Operational Check		Oil Pressure

- After one hour’s run:		Oil Leaks

- Cooling System

- Oil Temperature

- Commissioning Test:		25% of full load	2 hrs.

- 50% of full load	5 hrs.

- 75% of full load	8 hrs.

- 100% of full load	8 hrs.

- 110% of full load	1 hr.

- All commissioning and test results shall be recorded and compared with design data. A retest/commissioning shall take place if results are not satisfactory. All the tools, labour, POL, required for the testing and commissioning shall be provided by the Contractor at no extra cost. If required load is not available at site for testing the generators, the Contractor shall provide dummy load at site at no extra cost to the Employer. The correct functioning of the control equipment shall also be proved.

- Battery Charger

- Battery charger shall be static type and shall provide for both trickle and boost charging of the batteries when the engine is not in operation. The charger shall be of suitable capacity to fully recharge the completely discharged batteries within four hours at boost charge.

- Control Panel

- The Control Panel shall provide all the necessary control and monitoring devices of the Diesel Generating Sets. All the control and monitoring of the safety devices, alarms, protections, meters, lamps, etc. as mentioned in this Specifications and required as per good engineering practices for such an installation shall be provided in the Control Panel.

- 14.3 	Transformer Tests

- In addition to the insulation resistance test of the transformer, a   polarity and phase rotation test shall also be made. Buchholz relay shall be  tested for proper operation.  Di-electric test shall be carried out on  transformer oil prior to putting the same in operation.

- 14.4	HT/LT Switchboards

- Each circuit breaker shall be operated electrically and mechanically.  All interlocks and control circuits shall be checked for proper connections  in accordance with the wiring diagrams given by the manufacturer.

- The Contractor shall properly identify the phases of all switchgear and cables for connections to give proper phase sequence. Trip circuits shall be checked for correct operation and rating of equipment served. The correct size and function of fuses, disconnect switches, number of interlocks, indicating lights, alarms and remote control devices shall be in accordance with approved manufacturer drawings. Nameplates shall be checked for proper designation of equipment served. Protective relays shall be tested and set at site prior to commissioning of the equipment.

- 14.5 	Insulation Resistance Test

- Insulation  resistance  test  shall be made on all  electrical  equipment  by using a meggar of 500 volts for circuits upto 250 volts and 1000 volt  for circuits between 250 and 500 volts. For testing of 11 kV circuits, upto 5 kV meggar shall be used; the exact voltage shall be as advised by the equipment manufacturer unless otherwise advised by the Engineer.

- The insulation resistance values of cables, transformer, switchgears, etc., shall be as per BSS, IEEE, NEC, ICEA and Pakistan Electricity Rules.

- Before making connections at the ends of each cable run or joint between cables, the insulation resistance test of each cable section shall be made. H.T. cables shall be subjected to high voltage test as per recommendations of standard to which the cable is manufactured. Each conductor of a multi-core cable shall be tested individually with each of the other conductor of the group and also with earth. If insulation resistance test readings are found to be less than the specified minimum in any conductor, the entire cable shall be replaced and tests repeated on new cable.  If cable joint is provided, then each cable  section shall be tested, and joint made only after the tests have been made satisfactorily. Finally the completed cable length including the joints shall be tested.

- The transformer  and switchgears shall be given an  insulation  resistance measurement  test after installation, but before any wiring  is  connected.  Insulation tests shall be made between open contacts of circuit  breakers, switches and between each phase and earth.

- If  the  insulation  resistance  of  the circuit  under  test  is  less  than  the specified value, the cause of the low reading shall be determined  and removed. Corrective  measures shall include  dry-out procedure  by means  of  heaters, if equipment is found  to  contain moisture. Where corrective  measures are carried out, the insulation resistance readings shall be taken after the correction has been made and repeated twice at 12 hours interval. The maximum range for each reading  in  the  three successive  tests  shall  not exceed 20% of the average  value.  After all tests have been made, the equipment shall be reconnected as required. Polarity test shall be made on single pole switching devices.

- 14.6	Earth Resistance Test

- Earth resistance tests shall be made by the Contractor on the earthing system, separating and reconnecting each earth connection.

- If it is indicated that soil treatment or other corrective measures are required to lower the ground resistance values, the Engineer will determine the extent of such corrective measures.

- The electrical resistance of the ECC together with the resistance of the earthing leads measured from the connection with earth electrode to any other position in the complete installation shall not exceed one Ohm. Earth resistance test shall be performed as per Electrical Inspector's requirements. Where more than one earth electrode is installed, the earth resistance test of each electrodes shall be measured by means of resistance bridge instrument.

- 14.7 	Completed Tests

- After any equipment has been tested, checked for operation, etc., and  is accepted  by  the  Engineer the Contractor shall  be  responsible  for  the proper  protection  of that equipment so that subsequent testing  of  other equipment do not cause any damage to the already tested equipment.

- 14.8 	Expenses

- All expenses, i.e., traveling, documentation, boarding and lodging, allowances etc. for carrying out the tests and witnessing by the Engineer and Employer shall be borne by the Contractor and are deemed to have been included in the BOQ rates of the respective equipment(s) by the Contractor.

15.0	PAYMENT

No separate payment shall be made for work involved within the scope of this section unless specifically stated in the Bill of Quantities or herein.