SECTION - 8220

WIRING ACCESSORIES

1.0    	SCOPE OF WORK

The work under this Section consists of supplying, installing, and  commissioning  of all material and services of the complete Wiring Accessories including switches, switch sockets, etc., as specified herein, as shown on the Tender Drawings and explained in the Bill of Quantities.

The Contractor shall discuss the electrical layout with the Engineer and  coordinate at Site with other services for exact location  and position of all wiring accessories.

The wiring accessories such as switches, switch socket outlets, socket outlets and ceiling roses, etc. shall also comply with the General Specifications for  Electrical Works Sec. 8001 and with other relevant provisions of the Tender Documents.

2.0	GENERAL

The locations of the wiring accessories such as switches, sockets, etc. are tentatively shown on the drawings. The Contractor shall ensure the exact positions and locations of wiring  accessories  in coordination with other services drawings, as per site requirements and as directed by the Engineer. The Contractor shall be responsible  for  proper  functioning of  wiring  accessories  after installation and commissioning.

The description of switches, switch sockets, socket outlets etc. are given in the Bill of Quantities, stated as drawings and in this section. The Contractor shall submit sample of each and every item of wiring accessories for the approval of the Engineer.

3.0    	APPLICABLE STANDARDS/CODES

The  latest  edition  of  following  standards  &  codes  shall   be applicable  for  the materials specified within the  scope  of  this section :

BS  3676	- 	Switches for domestic and similar purposes.

BS  4343	-	Industrial plugs, socket outlets and couplers for AC

and  DC supplies.

BS  2135 	- 	Capacitors for radio interference suppression.

BS  67   	- 	Ceiling roses.

BS  546  	- 	2-pole and earthing pin plugs, socket outlets and socket 					outlet adaptors.

BS 1362	-	Specification for general purpose fuse links for domestic and similar purposes.

BS 1363

(Part 4-1995)	-	Specification for 13A fused connection units: switched and unswitched.

BS 5733

(1995)	-	Specification for general requirements for electrical accessories.

DIN EN

60669-1	-	Switches for household and similar fixed electrical installations.

4.0    	MATERIAL

4.1    	Switches/Blank Face Plates

Switches for controlling light and fan points shall be single pole,  rated  for  10 Amps, 250  volts AC. The body of the switches shall be of thermoplastic with faceplate suitable for flush mounting and colour as approved by the Engineer.  The switches shall be gang type having silver tipped contacts and shall operate with snap action.

Unless otherwise specified wherever switches control only the light points, these shall be plate type gang switches installed on common outlet boxes. Where only sheet steel back box is indicated on drawings, blank face plates shall be provided of same make and model as that of switches.

Where specified weather proof or metal front plates shall be used with single grid type switches. The plate shall be finished in specified colour or as otherwise directed by the Engineer.

The bell push switches shall be spring loaded type with the identification symbol embossed on it.

Two-way and intermediate switches shall be used to control lights from two or more different locations particularly in staircase as shown on the drawings.

4.2    	5A/15A Switch-Socket Outlets

Switch socket units shall be 3 pin, 5 Amps, 15 Amps 250V, AC with faceplate of colour as approved by Engineer. The outlets shall be heavy-duty type suitable for mounting on sheet steel outlet box.  The 15 Amps Switch socket outlets shall have sheltered live contacts and designed such that the earth pin of plug is engaged to socket earth before making of live contacts.

Where metal plate switches are installed, the switch socket units shall also be provided with front plate of similar design.

4.3	16A Schuko Socket Outlets

16 Amps Socket Outlets shall be 2 pin + earth, 250V AC German type (Schuko) socket outlets with faceplate of colour as approved by the Engineer. Duplex 16 Amps Schuko units shall consist of 2 Nos. 2 pin + earth German Type (Schuko) socket outlets prewired with 3(1x4.0 sq.mm) PVC cable with a common face plate of colour as approved by the Engineer.

The outlets shall be heavy-duty type suitable for mounting on sheet steel outlet box.  The 16 Amps Schuko Socket Outlets shall be designed such that the earth pin of plug is engaged to socket earth prior to making contact to the live contacts.

4.4	Duplex 13/5 Amps Switch – Socket Outlets

Duplex units shall consist of 2 Nos. 3 pin, 13/5 Amps, 250V AC switch socket outlets with face plate of colour as approved by the Engineer. The outlets shall be heavy-duty type suitable for mounting on sheet steel outlet box.

4.5	16A/32A/63A Industrial Socket Outlets

The 16A/32A or 63A, 230/400 V, single/ 3 Phase plus neutral & earth 3/5 pin, industrial type socket outlets shall be weather proof conforming to the standard and requirements of relevant IEC codes.

The socket outlets shall be of heavy-duty type suitable for outdoor installation. The socket outlets shall be mounted on polycarbonate enclosure and have gasketed cover and window, captive cover screw type. All industrial socket outlets shall be supplied with matching plugs.

  - Connection Units (Spur outlets)

Connection Units shall be used to supply power to appliances such as Fan coil units, Hand drier, Water heaters, etc., where so specified or shown on drawings.

It shall be rated for 13A, 250V AC or as shown on drawings/BOQ. The body shall be of thermoplastic material. Installation shall be surface/ concealed as required.

Face plate and colour to be as per approval of Engineer.

Connectors shall be of best quality (for Phase, Neutral and Earth) and suitable for the size of wiring.

The connection unit shall have the following features as per requirement in B.O.Q or as shown on drawing.

- 20 A Double Pole Switch

- Fuse – Rating as per requirement of appliance

- Neon Indication light

- Grommetted outlet on face plate suitable for flexible wiring connection to appliance

4.7	Fan Dimmers

The fan regulator/dimmer shall be made of low voltage electronic components with essential radio frequency compressor and shall be designed for smooth speed control/variation of fans. The regulators/dimmer and fan control switches shall be of same make and colour as that of the approved wiring accessories. The regulator/dimmer and fan-controlling switch shall preferably be mounted on same face plate. They shall be suitable for flush mounting on a sheet steel outlet back box.

4.8    	Sheet Steel Back Boxes

The sheet steel boxes for installation of switches, fan dimmers, socket, outlets and blank face plates shall be made of 16 SWG sheet steel having appropriate dimensions. The box shall have suitable arrangement for receiving the conduit(s). An earth terminal shall be provided for connecting at least three earth wires of 4-sq.mm size. The outlet box shall be finished in powder-coated paint. The sheet steel back box shall be as approved by the Engineer.

4.9    	Ceiling Roses

The ceiling roses shall be suitable for 5 amps 250 volts single-phase ac. It shall have white plastic moulded base plate and copper or brass terminals suitable for connecting at least two wires of 2.5 sq. mm size. The ceiling rose shall have a cover with cable inlet hole suitable for multicore PVC insulated and PVC sheathed cable.

5.0    	INSTALLATION

5.1   	General

The mounting heights of all wiring accessories are stated on the drawings. In case the mounting height is not mentioned, the instructions of the Engineer shall be obtained before fixing.

  - Wiring Accessories Installation

All wiring accessories such as Switches, Blank Face Plates, 5A/15A Switch Socket, 16A Schuko Socket Outlets, Duplex 13/5 Amp Switch-Socket Outlets, 16A/32A/63A Industrial Socket Outlets & Connection Units shall be installed on 1.63 mm (16 SWG) thick sheet steel box recessed in wall/column/floor. The faceplate shall be fixed on sheet steel box by means of flat head galvanized or brass screws sunk in the faceplate so as to finish flush with the surface. Matching screw caps shall be installed on the opening for screw in faceplates.

The industrial type sockets in polycarbonate enclosure shall be installed on wall as shown on drawing.

6.0       MEASUREMENT AND PAYMENT

6.1     	General

The Contractor's bid amount against each Bill of Quantities item as given below shall include supply, installation, testing, commissioning and completion for all work specified herein and/or as shown on the Tender Drawing related to the item.

6.2	5A/15A Switch Socket Outlets, 16A Schuko Socket Outlets, Duplex 13/5 Amps Switch Socket Outlets, 16A/32A/63A Industrial Socket Outlets & Connection Units

6.2.1   	Measurement:  Measurement shall be made for the total number of each type of socket outlet complete with sheet steel back boxes, polycarbonate enclosure and all accessories acceptably supplied and installed by the Contractor as a complete unit.

6.2.2   	Payment:  Payment shall be made for the total number of units measured, as provided above, at the Contract unit price each and shall constitute full compensation for supplying, installing, connecting, testing and completion of each type and rating of outlet including screws, screw caps, sheet steel box, polycarbonate enclosure, nuts, bolts and other accessories as required.