SECTION - 8211

HIGH TENSION CABLES

1.0	SCOPE

The work under this section consists of supplying, installing, testing and commissioning of all material and services of High Tension (HT) cables and accessories as specified herein or as stated on the Tender Drawings and in the Bill of Quantities.

The Contractor shall discuss the electrical layout with the Engineer and co-ordinate at site with other services for exact route, location and position of the HT cables.

The HT cable with accessories shall also comply with the General Specifications  for Electrical Works Section-8001 and with other relevant provisions of the Tender Documents.

2.0	GENERAL

The 15kV cables shall be three core, copper conductor, cross-linked polyethylene (XLPE) insulated, shielded, armoured or unarmoured as per requirements and overall sheathed. It shall be suitable for indoor and outdoor use in the transmission and distribution of electrical energy.

The cables shall be capable of operating continuously at a conductor temperature of not less than 90 oC and shall be suitable for 8.7/15 kV, 50 Hz in three phase grounded system in accordance with IEC 60502.

The cable shall be treated for vermin proofing and be protected against rodents during storage, laying and all protective pipes/ sleeves shall be plugged to attain the same after installation.

3.0	APPLICABLE STANDARD/CODES

The  following standards and codes shall be applicable for  the  materials within the scope of this Section:

IEC 60502	Power cable with extruded insulation and their accessories for rated voltages from 1 kV (Um = 1.2 kV) up to 30 kV (Um = 36 kV).

IEC 60540      	Test methods for insulation and sheaths of  electric cables and 	cords.

IEC 60228 	Conductors of insulated cables.

IEC 60332-1 	Tests on electric cable under fire conditions – Part 1

IEC 60332-3	Tests on electric cable under fire conditions – Part 2

4.0 	MATERIAL

4.1 	15kV Cable

The cable shall meet the following specifications:

Nominal/System Voltage 	- 	11 kV

Frequency                 		- 	50 Hz

System                    		- 	3 phase with solidly grounded,

star point of transformers.

Conductor Size	-	Sq.mm.  As given in BOQ,

Number of Cores		- 	3

Rated Voltage               	- 	15/8.76 kV phase to phase/phase to 					ground.

Continuous operating		-	90oC

temperature of conductor

Conductor material           	-    	Copper stranded

Insulation                  		-    	Cross-linked polyethylene (XLPE)

Shielding                  		-    	Copper tape

Jacket                    		-    	PVC

Armouring                 		-    	Galvanized steel wire

Oversheathing               	-    	Extruded PVC

Phase identification           	-    	Red, Yellow, Blue

4.1.1	Conductor

The conductors shall be of high conductivity electrolytic copper, stranded in accordance with specified standard.

4.1.2	Insulation

The insulation shall be cross-linked polyethylene extruded over   the conductor. The insulation shall be laid to avoid any gap/air  pockets between the conductor and insulation. The insulation shall be colour coded red, yellow and blue for phase identification.

The  insulation  shall  be easy to strip from  individual  conductors  and  to separate for jointing/termination purposes.

4.1.3 	Shielding

Each  core  shall  be  shielded by  a  layer  of  semi-conducting  material applied directly over the insulation. The semi-conducting insulation  shall be covered by a bare copper tape applied with suitable overlapping.

Phase identification tape of red, yellow and blue colours shall be wrapped over the copper shield.

4.1.4	Assembly

The three insulated conductors shall be assembled with PVC or any non-hydroscopic filler and bounded with tape. The tape binder shall  then  be covered with extruded PVC jacket. The PVC jacket shall be padded with a suitable material before application of armour.

4.1.5	Armour

Armouring shall be provided with single layer of galvanized steel wire to provide cable  protection  and also act as a low  resistance  earth  return path. The armouring shall be covered with binder tape. The armour shall be of appropriate size to carry the system fault current.

4.1.6	Oversheath

The entire cable assembly shall be covered with a PVC jacket of thickness  not less than 2.5 mm. The colour of the jacket shall be  black.

Embossed marking on the oversheath at 3 meters intervals shall give the following information:

-	name of Manufacturer

-	year of  Manufacture

-	size of cable in sq.mm.

-	voltage grade

-	type of cable i.e. Cu./XLPE/SWA/PVC

4.2	Factory Tests

Physical and electrical acceptance tests in accordance with applicable standard shall be carried out at the manufacturer works in the presence of Engineer. Three copies of test reports will be furnished to the Engineer, which shall include brief description of tests, test records and results.

4.3	Termination Kits

Termination kits for 15 kV cable shall be indoor/outdoor type as per requirement and recommended by cable manufacturer and as approved by Engineer. The termination kits shall be complete with all materials and meet all the requirements of IEC Publication 60060, 60230 & 60270.

Termination kits shall be hot or cold shrink type suitable for the approved 15 kV HT cable and ambient conditions described in Section-8001. The termination kit shall provide reliable water proofing, mechanical and electrical protection after installation. The material and components of termination kit shall perform satisfactory without distress under normal conditions, cyclic loading and fault conditions.

4.4	Cable Accessories

All cable accessories shall be provided for the complete cabling system without any additional cost unless specifically mentioned in BOQ. These shall include but not limited to the items such as saddles, clamps, fixing channels, connectors, clips, lugs, tapes, solder, identification tags, bushes, glands etc.

4.5	Cable Reels

The   cable  shall  be supplied  in  non-returnable,  mechanically  strong, sea/rail/road worthy, wooden or metallic cable drums, protected  against weather. The cable drum should bear the markings for cable type,  cable size,   voltage   grade,  year  of  manufacture,  name   of   manufacturer,  direction   of  unreeling,  and  any  other  additional  marking   normally provided  by  the  manufacturer.  Cable  ends  on  cable  reels  shall   be protected by means of suitable seal.

4.6	Cable Markers

Above ground cable markers made of Grade-25 reinforced concrete shall be erected at a maximum interval of 200 metres along the straight trench, at each bend and joint box for indicating the presence of underground cables. Where the trench changes its direction two number of markers shall be installed one in each direction to indicate the two directions of the trench. At the joint  box, additionally a symbol shall be engraved just beneath the letters HT or LV to indicate the presence of the joint box.

The cable markers shall be finished in grey paint. The letters and symbols for indication shall be engraved in concrete on both sides. Letters shall be HT or LV for medium voltage or low voltage cable. The colour of the engraved letters and symbol shall be red. The dimensions of the markers shall be as shown on the drawing and shall be installed in the ground as shown.

5.0	INSTALLATION

5.1 	General

All installation material, labour, tools and accessories for cable installation   shall be furnished by the Contractor. The cable and accessories shall  be  installed as described in these Specifications, drawings and in  accordance  with  manufacturer's instructions.

Necessary precautions for safety of cables shall be taken during the laying of cables to avoid scratches/ cuts to the cable surface. Pulling force on cable at all times shall remain well within the manufacturer’s recommended limits.

The exact cut lengths for  cable shall be confirmed by the Contractor by actual measurements at site prior to the commencement of manufacturing.  The cable lengths where shown on the drawing/BOQ are tentative and only for general guidance. The Contractor shall be solely responsible for furnishing correct lengths of cable to avoid joints in cable length.

No separate payment for such joints shall be admissible.

Prior to installation of jointing and termination kits, the cable lengths shall be checked and tested to ensure that the cables are in sound condition, and no damage has been done during handling and installation. After the  H.T. cable and jointing/termination kits are installed, it shall again be  tested prior to commissioning and in accordance with recommendations  of  standard to  which  the  cable  is manufactured.

5.2 	Underground Cables

The  cables to be installed directly underground shall be laid  in  trenches in  single  tiers. Unless shown specifically on the drawing the depth of cable   below finished ground level shall be 900 mm minimum  measured from  the top of the largest cable to the general ground level. The burial depth  may  be  increased  as  required due  to  site  conditions  or  when crossing  other  service pipes and roads. Burial depth less than 900mm and more than 1500mm shall require Engineer's approval.

When cables cross road, paved area, other services or other cables,  they shall be laid in protective pipes of required size. Cables entering  the buildings shall also be laid in protective pipes. All the protective pipe  ends, after installation of cables, shall be plugged water tight by means  of sealant as approved by the Engineer. A minimum clearance of 250mm vertically and 500mm horizontally shall be maintained between cables and other services.

The cable trench shall be excavated as per site conditions taking the best possible route as approved by the Engineer. Before laying of cables in the trench, the bed of the trench shall  be leveled and filled with a 100mm thick layer of fine sand  (1.3mm diameter maximum particles size). The sand layer shall be levelled and the cables placed thereon. The cables shall be covered with a layer of fine sand 100mm thick measured above the top of the largest cable. The cable protective tiles placed above the top of sand cover shall be of class-C cement concrete, minimum 50mm thick and 300mm square.  Good quality bricks of proper strength and shape, well formed can also be used for the purpose of protection. The tiles or bricks  shall be placed over the sand layer end to end to cover the  entire length  and  breadth  of the cable trench. After  the  concrete tiles/bricks  are placed, the remainder of the trench shall be backfilled with earth in layer 300mm thick. Each layer shall be thoroughly tamped and compacted.

A PVC warning tape shall be provided at 300 mm below normal ground level covering the entire length and breadth of the trench. The warning tape shall be yellow in colour with markings of danger and voltage of the cables printed in black.

Cable identification tags of water resistant material with indelible marking shall be fixed to cables with ties at a maximum of 20 metres interval along  the cable length for identification of cable and circuit. The earth  continuity conductor/counterpoise conductor shall  be  laid in the trench with the cable. The Contractor shall submit to  the Engineer for approval, schedule  of  cable  markers showing location of marker and instructions on each.

Sufficient  slack  shall be left in cables for which purpose the cut  lengths of  cables  shall allow about 3% more in the  measured  lengths  between terminations.  At  underground  joint  box, ample slack  shall  be  left  to prevent straining of cable joints due to settlement of the cable trench.

The cut lengths of cables wherever stated are only as a guide. The Contractor  shall  measure lengths between terminations  of  each  circuit and if the discrepancy between measured lengths at site and where  given on  the drawing differ by  more than  5%, the Contractor  shall report  to Engineer and act  as directed. Cables, whether installed underground,  or in  cement  concrete trenches, shall not be bent to a radius less  than  that recommended by the cable manufacturers.

5.3 	Cable Markers

The cable markers shall be installed on finally compacted trench at mentioned distances.

Above ground, cable markers shall be erected at a 200 metre interval along the straight trench, and at each bend and joint box for indication of presence of underground cable. For more than one metre wide trenches, cable markers shall be provided at both edges of the trench. The cable marker shall bear the necessary instructions indicated in approved colours.

The Contractor shall submit to the Engineer for approval, schedule of cable markers showing location of marker and instructions on each marker.

6.0 	MEASUREMENT AND PAYMENT

6.1	General

The  Contractor's  bid amount against each item of Bill of  Quantities  as given  below  shall include supply,  installation,  testing,  commissioning and  completion  for  all work specified herein and/or  as  shown  on  the Tender Drawing related to the item.

6.2 	HT Cables

6.2.1 	Measurement

Measurement shall be made of the total running feet of H.T. cables acceptably supplied and installed by the Contractor and which has satisfactorily passed all the required tests prior to   and   after installation.

6.2.2 	Payment

Payment  shall  be  made for the total running feet  of  the  HT cables as provided above at the Contract unit price  and  shall  constitute full compensation  for supply, installing, connecting, testing and commissioning of the HT cables including cable identification tags, ties, colour sleeves, cable glands, lugs, and all accessories complete with plugging of protective pipes/ sleeves ends for water tightening.

6.3 	HT Termination Kits

6.3.1 	Measurement

Measurement shall be made for each type of H.T termination kit acceptably supplied and installed by the Contractor as a complete unit.

6.3.2	Payment

Payment shall be made for the number of units measured as  provided above at the Contract unit price each and shall constitute   full compensation for supplying, installing, connecting, testing    and commissioning of HT termination kit including all   installation accessories, supports, as required etc.

6.4	Cable Trenches

6.4.1	Measurement

Measurement shall be made for the total cubic feet of excavation work of cable trenches acceptably completed by the Contractor according to specification and as shown on drawing.

6.4.2	Payment

Payment shall be made for the total cubic feet of excavation of cable trenches measured as stated above at contract unit price and constitute full compensation for all the works related to the item.

No separate payment shall be made for the under mentioned specified work related to the excavation of cable trench. The cost thereof shall be deemed to have been included in quoted unit rates of the excavation for cable trenches:

-	Dewatering during excavation and backfilling.

-	Providing and filling of fine sand in trenches.

-	Providing and laying of protective concrete tiles or bricks in

trenches.

-	Compacted backfilling of trenches with specified material and disposal of surplus and rejected material.

- Providing and laying of PVC warning tape.

6.5	Cable Markers

6.5.1	Measurement : Measurement shall be made for the total number of cable markers acceptably supplied and installed by the Contractor as a complete unit.

6.5.2	Payment :  Payment shall be made for the total number of cable markers as provided above at the contract unit price and shall constitute full compensation for supplying & installing reinforced concrete cable markers, excavation, backfilling, concrete curing, and painting etc.