SECTION – 5216

WATER SUPPLY PIPES, PIPE LAYING AND APPURTENANCES

- SCOPE

- MATERIALS

- APPROVAL OF MATERIAL AND EQUIPMENT

- INSTALLATION

- FLUSHING

- LEAKAGE TEST

- RETESTING AFTER BACKFILL

- PIPE LINE DISINFECTION

- FINAL FLUSHING

- SAMPLING AND TESTING

- CLEAN UP

- INDICATION PLATES

- WASHOUTS

- AIR VALVES

- MEASUREMENT AND PAYMENT

5216	WATER SUPPLY PIPES, PIPE LAYING AND APPURTENANCES

1	SCOPE

The work covered by this Section of the specification consists in furnishing all plant, labour, equipment, appliances and materials and in performing all operations in connection with water supply lines and appurtenances in strict accordance with this section of the specifications and the applicable Drawings.

2	 MATERIALS

Material shall conform to the respective specifications and other requirements specified hereinafter and shall be new and unused.

01	Cast Iron Pipes and Fittings

Cast iron pipes and fittings shall comply with ISO 13-1978 (E) or B.S. 78 for spigot and socket vertically cast pipes, B.S.1211 for spigot and socket spun iron pipes and B.S. 2035 for flanged pipes.

02 	Asbestos Cement pipes, Fittings and Specials

These shall conform to International Organization for Standardization Recommendation R160 "Asbestos Cement Pressure Pipe and joints" or British Standard Specification 486 "Asbestos Cement Pressure Pipe" or to Pakistan standard specification No. PS. 428 : 1984 of the class capable of withstanding a 400 ft. head test pressure. Short lengths of pipe machined overall shall be used at fittings for tying in.

The fittings and specials for asbestos cement pipes shall be cast-iron conforming to British Standard Specification 78: PART 2 Fittings: "Cast Iron Spigot and Socket Fittings", Class AV, except that the fittings and specials shall have the shapes, dimensions and tolerance required to fit the asbestos-cement pipes. Fittings and specials for asbestos-cement pipe shall be supplied by the manufacturer of the asbestos-cement pipe.

Rubber ring shall conform to Pakistan standard specification No. PS. 1915: 1987.

03	Galvanized Iron Pipes and Fittings

The galvanized iron pipes shall strictly conform to B.S. 1387 Specifications for "Steel Tubes and Tubulars suitable for screwing to B.S. 21 pipe threads" and shall be of medium grade. All screwed pipes and sockets shall conform B.S. 1740. A complete and uniform adherent coating of zinc white will be provided for galvanized iron pipes and fittings.

04 	M.S Pipe

All mild steel pipes shall conform to ASTM designation A53, schedule 40 "standard specification for welded and stainless steel pipe". All pipes shall be internally cement mortars lined and externally bituminous coated.

M.S. short pieces shall be flanged at both ends. The flanges shall conform to B.S. 4504, part 3 (PN 16). M.S. pipe pieces shall be externally protected by applying two coats of red oxides (of approved quality) and bituminous coating (grade 10/20) at the rate of 0.4 lb/Sq.ft.

05 	Unplasticised Polyvinyl Chloride Pipe and Fittings

Unplasticised polyvinyl chloride (uPVC) and fittings if approved by the Engineer shall confirm to BS 3505 pipes shall be class C: Pipe and fittings shall not be stored directly exposed to sunlight handled or laid in conditions where ambient temperatures may cause distortion or damage. In extreme conditions, pipe and fittings may have to be stored under water.

- Joints for Unplasticised Chloride Pipe

Joints for unplasticised polyvinyl chloride pipe shall be the Z type consisting of a socket with rubber gasket, or approved equal, and assembled in accordance with the pipe manufacture’s recommendations.

## Polyethylene (P.E.) Pipes and Fittings

High-density polyethylene pipes (HDPE) and fittings shall conform to ISO 4427/DIN 8075 standards. Material, diameters, wall thickness shall be as indicated in 4427/DIN 8074. Tests to be performed for pipes shall be Heat revision, Short term hydrostatic pressure test and Tensile strength and for P.E. compounds shall be Elongation at break, Melt flow rate and Density test.

Warning tape shall be provided for lying over P.E. pipes. It should be single fold, 0.02 inch thick and 2 inch wide, with warning for digging continuously printed in Urdu language. The tape shall be placed one foot above the P.E. pipe.

Bricks on edge shall be placed on the P.E. pipes along its edge after it is laid in order to avoid any damage to the pipe.

08	Sluice (Gate) Valve

Valves shall be wedge gate valves conforming to British Standard Specification 5163. Ends of valves shall be suitable for the type of pipe to which the valves will be connected.

09	Check Valves

Check valve shall comply with the requirements of BS 5153 latest revision for pressure rating of 16 bar. The valve shall be of swing type and shall be of quick acting single door type.

10	 Fire Hydrants

The metal of the fire hydrant shall conform to B.S. 750 and shall be of screw down streamline pattern. The body shall be best quality, closed grain, grey cast iron with spindle of manganese bronze having tensile strength of not less than 11.0 tons per square inch machined from solid rolled bars, the seating valves and other parts shall be of best quality gun metal with Brinell Hardness No. 80. The direction of closing shall be by clockwise rotation and outlet shall have screwed joint for accommodation 2 1/2" dia hose connection. Inlet flanges of hydrant shall be suitable for jointing with flanges of hydrant bends and tees. All fire hydrants shall be coated with three coats of solution from an approved manufacturer to give a uniform protective coating on cast iron.

3	APPROVAL OF MATERIALS AND EQUIPMENT

As soon as practicable but within 30 days after receipt of notice to proceed and before any materials or equipment are purchased, the Contractor shall submit for approval by the Engineer a complete schedule, in triplicate, of materials and equipment to be incorporated in the work, together with the names and addresses of the manufacturers and their catalogue cuts, diagrams, drawings, and such other descriptive data as may be required by the Engineer. No consideration will be given to partial lists submitted from time to time. Approval of materials and equipment under deviations from the specifications shall not be granted unless the attention of the Engineer has been directed to the specific deviations. Laboratory results and certifications, specified or otherwise required, shall be submitted prior to delivery of the material and equipment to site.

4	 INSTALLATION

01	Handling

Pipe and accessories shall be handled in such a manner as to ensure their delivery to the trench in sound, un-damaged condition. If any pipe or fitting is damaged, the repair or replacement shall be made by the Contractor at his expenses in a satisfactory manner. No other pipe or material of any kind shall be placed inside of a pipe or fittings. Pipe shall be carried into position and not dragged. The interior of pipe and accessories shall be thoroughly cleaned of foreign matter before being lowered into the trench and shall be kept clean during laying operations by plugging or other approved method. Before installation, the pipe shall be inspected for defects. Material found to be defective before or after laying shall be replaced with sound material without additional expense to the Employer. Rubber gaskets that are not to be installed immediately shall be stored in a cool dark place and protected against the direct rays of the sun.

02	Cutting of Pipe

This shall be done in a neat and workman-like manner without damage to the pipe. Unless otherwise authorized by the Engineer or recommended by the manufacturer, cutting shall be done with a mechanical cutter of approved type. Wheel cutters shall be used wherever practicable.

03 	Location

Where the location of the water pipe is not clearly defined by dimensions on the Drawings, the water pipe shall be located as directed by the Engineer.

04	Deflection

Maximum allowable deflections from a straight line or grade, as required by vertical curves, horizontal curves, or offsets will be 2o degrees for Asbestos Cement Pipe unless other- wise recommended by the manufacturer. If the alignment requires deflections in excess of the specified limitations, special bends or a sufficient number of shorter lengths of pipe shall be furnished to provide angular deflections within the limit setforth, as approved.

05 	Placing and Laying

Pipe and accessories shall be carefully lowered into the trench by means of derrick ropes, belt slings, or other suitable equipment. Under no circumstances shall any of the water line materials be dropped or dumped into the trench. Care shall be taken to avoid abrasion of the pipe coating. Poles used as levers shall be of wood and shall have broad flat faces to prevent damage to the pipe. Except where necessary in making connections with other lines or authorized by the Engineer pipe shall be laid with the bells facing in the direction of laying. The full length of each section of pipe shall rest solidly upon the pipe bed, with recesses excavated to accommodate bell coupling and joints. Pipe that has the grade or the joint disturbed after laying shall be taken out and relaid. Pipe shall not be laid in water shall be kept out of the trench until the materials in the joints have hardened or until chaulking or jaunting is completed. When work is not in progress, open ends of pipe, fittings, and valves shall be securely closed so that no trench water, earth, or other substances will enter the pipes or fittings. Where any part of a coating or lining is damaged, the repair shall be made by the Contractor at his expense in a satisfactory manner. Pipes shall be installed in accordance with recommendations of the pipe manufacturer. Pipe ends left for future connections shall be valved, plugged or capped, and anchored, as shown or as directed, where connections shall be made by using specials and fittings to suit the actual conditions.

06	 Jointing

The joints shall be in accordance with the recommendations of the manufacturer or as approved by the Engineer.

Connections between different types of pipes and accessories shall be made with transition fittings where recommended by the pipe manufacturer.

Service connections shall be made as indicated and in accordance with the recommendations of the pipe manufacturer.

07	Setting of Fire Hydrants, Valves and Surface Boxes

Fire hydrants shall be located and installed, as shown. Hydrants shall be set plumb and in accordance with the manufacturer's instructions.

Valves and surface boxes shall be installed as shown or directed, and shall be set plumb. Surface shall be centered on the stems or operators. Concrete, concrete pipe, brick, brick ballast used in chambers shall conform to the relevant clause of the Specification. Where feasible, valves or operators shall be located outside the area of roads and streets. Earth fill shall be carefully tamped around each valve box to the satisfaction of Engineer on all sides of the box, or to the undisturbed trench face if less than 4 ft.

Hydrants and valves shall have the interiors cleaned of all foreign matter before installation. Surface boxes shall be lighted and the hydrant or valve shall be inspected in open and closed positions to ensure that all parts are in working condition.

08	Thrust Blocks

Plugs, caps, tees, bends and fire hydrants shall be provided with concrete thrust blocks. Backing shall be placed between solid ground and the hydrant or fitting to be anchored. The area of bearing shall be as shown on the Drawing. The backing shall be so placed that fitting joints shall be accessible for repair. The concrete shall be class C plain cement concrete.

09	Pipe Bedding

Fine sand as pipe bedding material shall be used for A.C. pipe and C.I. fittings. The sand shall be free from clay, site, salts, organic impurities and debris. Approval of pipe bedding materials shall be obtained by the site Engineer prior to placing.

10	Pavement Restoration

The Contractor shall restore paved surface which have been cut under this contract, as part of the work under the excavation items and at no extra cost to the owner/employer.

5	FLUSHING

The Contractor shall provide facilities for flushing the line. Water for flushing the line shall be arranged by the Contractor. Flushing of line shall be done section by section. For each valved section of pipeline the Contractor shall make a temporary hose connection between the water pipeline and the pipeline under test. Water shall be pumped into the section flushed. Other arrangements for storing and pumping of water shall be subject to the approval of Engineer. Due precautions shall be taken by the Contractor for the disposal of water. The pipeline shall be flushed by keeping all the branching pipes open. Flushing shall be continued until clean water starts flowing through the other end. Section by section, the entire pipeline shall be flushed at a minimum flushing velocity of 2.5 ft./sec.

6	LEAKAGE TEST

Flushing of the pipeline shall be followed by a leakage test. The Contractor shall provide facilities for performing the leakage test. Water and pumping facilities shall be provided by the Contractor. Before the testing of pipeline the Contractor shall ensure that concrete backing blocks have been provided where necessary. The test shall be performed only after all concrete work in contact with pipe to be tested has set for a minimum of 24 hours. All joints shall be left exposed. Leakage test shall be performed by keeping the end of the pipeline closed by proper plugs blocked to resist 150 per cent of the working pressure. While filling the line all valves and openings shall be kept open and water shall be filled in slowly. When the pipeline is completely filled with water and all air expelled, water shall be pumped into the pipeline to a minimum pressure of 150 percent of actual working pressure and the test pressure shall be maintained for at least 1 hour. Each and every joint shall be inspected for leaks and for all visible leakage and displacement leakage test shall be performed by the Contractor, for the newly laid pipeline. A measured quantity of water shall be pumped into the pipeline. No piping installation will be accepted until the leakage is equal or less than the number of imperial gallons per hour as determined by the formula:

L = 0.00054 ND / P

L = Leakage in Imperial Gallons

N = Number of joints

D = Nominal diameter of pipe in inches

P = Average test pressure (psi) during test

In the event of the pipeline failing the leakage test, the Contractor shall locate and repair the defective pipe, fitting or joint at his expenses. For dewatering the line for repairs the Contractor shall follow the instructions given by the Engineer for disposal of water. After repairs of the line, the Contractor shall retest the line. The line will not be accepted until it passes the leakage test.

7	RETESTING AFTER BACKFILL

After the pipe trench has been backfilled, the entire length shall be subjected to a leakage test as a whole unit. The Contractor shall repair the line if it fails to pass the leakage test requirements specified hereinbefore. The test shall be repeated and repairs effected until the pipeline passes the leakage test.

8	PIPELINE DISINFECTION

01	General

The Contractor shall furnish all equipment, labour and material for the proper disinfection of the pipeline. Disinfection shall be accomplished by chlorination after the lines have been tested for leakage but before they have been connected to the main system. Disinfections of the pipelines shall be done in the presence of the Engineer's representative with equipment approved by him.

02	Chlorination

A chlorine and water mixture shall be supplied by means of a solution feed chlorination device. The chlorine solution shall be applied at one end of the pipeline through a trap, in such a manner that as the pipeline is filled with water, the dosage applied to the water entering the pipe shall be atleast (25 p.p.m) or enough to meet the requirements given hereinafter.

03	 Retention Period

Chlorination water shall be retained in the pipeline for a period of at least 24 hours. After the chlorine treated water has been retained for the required time, the chlorine residual at the pipe extremities and at such other representative points shall be at least 10 parts per million. This procedure shall be repeated until the required residual chlorine concentration is obtained.

04	Chlorination of Valves

During the process of chlorination the pipeline, all valves or other appurtenances shall be operated while the pipeline is filled with the heavily chlorinated water.

9	FINAL FLUSHING

Following complete disinfection of the pipeline, all treated water shall be thoroughly flushed from the pipeline at its extremities. Treated water and water used for flushing the pipelines shall be disposed of in a manner instructed by the Engineer. Fresh treated water shall be filled in the line and water tested from presence of coliform. the test result should indicate negative coliform presence. If the test indicates any positive coliform, the entire process of disinfection shall be repeated or improved upon until coliform free samples are obtained.

10	SAMPLING AND TESTING

Disinfection of the pipeline and appurtenances shall be the responsibility of the Contractor. The first set of samples will be collected for analysis by the Engineer. Should the samples reveal presence of coliform the Contractor shall again disinfect the pipeline and appurtenances at no extra cost to the Employer for sampling and testing for subsequent retests until coliform free samples are obtained. The charges for resampling and retesting shall be recovered from the Contractor.

11	CLEAN-UP

Upon completion of the installation of the water supply lines, distribution system and appurtenances, all debris and surplus materials resulting from the work will be removed and disposed off in a manner satisfactory to the Engineer

12	INDICATION PLATES

The indication plates shall be installed in accordance with the drawings and as directed by the Engineer.

13	WASHOUTS

The design and locations of washouts shall be illustrated on the Drawings to be approved by the Engineer. Exact positioning shall be determined with regard to topography and to the approval of the Engineer. At least 10 ft. of the washout pipework, inclusive of the isolating valve, measured from the centre line of the pipeline, shall be laid at the same time as the pipeline and suitably capped to preventingress of foreign material. The minimum gradient for the washout pipework shall be 1 in 100.

14	AIR VALVES

a)	 Double orifice Air Valves

These shall be designed to meet the following conditions:

- expulsion of air during charging of the pipeline

- admit air during emptying of the pipeline to avoid the occurrence of negative pressure

- expulsion of air accumulated at summit points along the pipeline under normal operating conditions

First two conditions shall be met by the employment of a large orifice capable of handling large volumes of air at high flow rate, and the third condition by a small orifice capable of discharging small quantities of air as they accumulate.

The large orifice shall be sealed by a buoyant rigid ball and the chamber housing shall be designed to avoid premature closing of the valve by the air whilst being discharged. The small orifice shall be sealed by a buoyant ball at all pressures above atmospheric except when air accumulates in the valve chamber.

b)	Single Orifice Air Valves

These shall be designed to carry out the function described above. Each valve shall be provided with only a small orifice which shall operate in the same manner as that in a double acting air valve.

Valves with air intake or exhaust facilities shall have approved screening arrangements to prevent the ingress of air borne sand.

The nominal pressure shall range between NP 16 and 25.

Body ends shall be flanged with raised faces and drilled according to BS 4504 for the nominal pressure specified or indicated in the Drawings.

The materials for the valves shall be as follows:

Cast iron body cover and cowl: for small orifice, cast iron with gunmetal seat with rubber covered ball or other approved; for large orifice, cast iron with rubber seat and vulcanate covered ball or other approved.

15	MEASUREMENT AND PAYMENT

Measurement and payment of pipework, fittings, specials and appurtenances will be made in accordance with the provisions of this clause specified hereinafter.

01)	Pipe work

a)	Method of Measurement: Measurement will be made for the number of running feet of Asbestos cement, uPVC, cast iron and M.S. pipes including fittings, accessories and flanges acceptably installed complete in all respects as per relevant Drawings or as directed by the Engineer.

b)	Basis of Payment: Payment will be made for the running feet of pipework as measured above at the Contract Unit price and shall constitute full compensation to provide, handle, lay and joint asbestos cement, uPVC and cast iron pipes including fittings, flushing, leakage testing before & after backfilling, final flushing and all other work related to the item.

02	Service Connection

- G.I. Pipe and Fittings

a)	Method of Measurement: Measurement will be made for the number of linear feet of galvanized iron pipe including fittings acceptably installed complete in all respects as per relevant Drawings or as directed by the Engineer.

b)	Basis of Payment: Payment will be made for the number of linear feet of galvanized iron pipework as measured above at the Contract Unit Price of each unit and shall constitute full compensation to provide, handle, lay, joint and test galvanized iron pipe, fittings, including sleeves, nuts, sockets, plugs, bitumen coating with Polyethelene tape and all other work related to the item.

ii)	Ferrule Assembly

a)	Method of Measurement: Measurement shall be made for the number of ferrules acceptably installed complete in all respects as per relevant Drawings or specifications.

b)	Basis of Payments: Payment shall be made for the number of ferrules measured as above at the contract unit price for each unit and shall constitute full compensation for providing, tapping, drilling, fixing including M.S. straps, Saddles, and all other work related to the item to make complete house connection.

03	Pipe Fittings and Specials

a)	Method of Measurement: Measurement will be made for the number of pounds of fittings and specials acceptably installed in pipework complete in all respects as per relevant drawings or as directed by the Engineer.

b)	Basis of Payment: Payment will be made for the number of pounds of fittings/specials as provided above at the Contract Unit Price and shall constitute full compensation for the cost of providing, handling, fixing, jointing, disinfecting, respective type of fitting/special, and all other work related to the item.

04	Sluice (Gate) Valves

a)	Method of Measurement: Measurement will be made for the number of sluice (gate) valves acceptably installed complete in all respects as per relevant Drawings.

b)	Basis of Payment: Payment will be made for the number of sluice (gate) valves measured as above at the Contract Unit Price for each unit and shall constitute full compensation for providing, handling, fixing and jointing and all other work related to the item including construction of chamber as shown on drawings.

05	Check Valves

a)	Method of Measurement: Measurement will be made for the number of check valves acceptably installed complete in all respects as per relevant Drawings.

b)	Basis of Payment: Payment will be made for the number of check valves measured as above at the Contract Unit Price for each unit and shall constitute full compensation for providing, handling, fixing and jointing and all other work related to the item including construction of chamber as shown on drawings.

06	Fire Hydrants

a)	Method of Measurement: Measurement shall be made for the number of fire hydrants acceptably installed complete in all respects as per relevant Drawings.

b)	Basis of Payment: Payment will be made for the number of fire hydrants measured as above at the Contract Unit Price for each unit and shall constitute full compensation for providing, handling, fixing and jointing and all other work related to the item including construction of chamber.

07	Indication Plates

a)	Measurement will be made for the number of indication plates acceptably installed complete in all respects as per relevant drawings.

b)	Basis of Payment: Payment will be made for the number of indication plates measured as above at the contract unit price for each unit and shall constitute full compensation for providing handling, fixing and all other work related to the item.

08	Washouts

a)	Method of Measurement: Measurement will be made for the number of washouts acceptably installed including construction chamber complete in all respects and as approved by the Engineer.

b)	Basis of Payment: Payment will be made for the number of washouts measured as above at the contract unit price for each unit and shall constitute full compensation for providing handling, fixing and all other work related to the item including construction of chamber.

09	Air Valves

a)	Method of Measurement: Measurement will be made for the number of air valves acceptably installed complete in all respects and as approved by the Engineer.

b)	Basis of Payment: Payment will be made for the number of air valves measured as above at the contract unit price for each unit and shall constitute full compensation for providing handling, fixing and jointing related to the item including construction of chamber.

10	Sand Cushion

a)	Method of Measurement: Measurement will be made for the number of cubic foot of sand acceptably placed complete in all respects and as approved by the Engineer.

b)	Basis of Payment: Payment shall be made for the number of cu.ft of sand measured as provided above at the contract unit price per cu.ft and shall constitute full compensation for all work related to the item.

- Thrust Blocks

a)	Method of Measurement: Measurement will be made for the number of cubic foot of class ‘C’ concrete acceptably placed complete in all respects and as approved by the Engineer.

b)	Basis of Payment: Payment shall be made for the number of cu.ft of class ‘C’ concrete measured as provided above at the contract unit price per cu.ft and shall constitute full compensation for all work related to the item.

12	Concrete Encasement

a)	Method of Measurement: Measurement will be made for the number of cubic foot of class C concrete acceptably placed complete in all respects and as approved by the Engineer.

b)	Basis of Payment: Payment shall be made for the number of cu.ft of class C concrete measured as provided above at the contract unit price per cu.ft and shall constitute full compensation for all work related to the item.