SECTION - 5400

MANHOLE, CATCH PITS AND VALVE CHAMBERS

WITH C.I. COVER AND FRAME

#### SCOPE OF WORK

- MATERIALS

3. 	APPLICABLE SECTIONS OF SPECIFICATIONS

- CONSTRUCTION

- DAMP- PROOFING

- STUBLINES

- COVERS

- MANHOLE STEPS

9. 	MEASUREMENTS AND PAYMENT

1	SCOPE OF WORK

This section covers standard, drop, and special sewer manholes. The work to be done under this section of the specifications includes furnishing all plant, labor, equipment, appliances, material and performing all operations required in connection with construction of manhole, valve chamber, or Grease trap etc., including provision and installation of cast iron cover with frame, ladder rungs, valves, etc., complete as specified herein, or as shown on the drawings, or as directed by the Engineer.

The work consists of constructing manholes for sewerage and valve chambers of water supply at positions shown on the plans or where otherwise directed by the Engineer, and in accordance with the Detailed Drawings supplied from time to time, complete in all respects.  The Contractor shall furnish all plant, labour equipment and materials in performing all operations in connection with the construction of manholes/valve chambers.

The various items of work involved in the construction of manholes and valve chambers shall be carried out strictly in accordance with respective technical specifications laid down for the item of work in these tender documents.

  - MATERIALS

| ## Concrete | Materials, handling, forms, finishing, curing, and other work as specified in Section 2100, 2200 or 2300 Concrete. |
| --- | --- |
| Reinforcement | As indicated on drawings. |
| Portland cement | ASTM C150 |
| Sand | Concrete sand (fine aggregate) sieved through 8 mesh screen |
| Mortar | One part Portland cement, 3 parts sand, ¼ part hydrated lime, ASTM C-207 |
| Non-shrinkable Mortar | Premixed or job mixed; job mixed shall be one part shrinkable correcting aggregate, one part Portland cement and one part sand. |
| Gaskets |  |
| ### Mastic | Enough material shall be applied to fill the joint so that a minimum of ¼ inch bead is visible, to be smoothened off after completion. |
| ### Flexible joint | Preformed “O” ring; butyl rubber or bituminous polymers are acceptable. Natural rubber is not acceptable. |
| ### Bricks | Bricks shall be 1st class burnt bricks as per requirements of specifications No. 4200. |
| ### Wall/slab thickness | Thickness shall be in accordance with those indicated on drawings. |

Cast iron frame shall conform to the specifications as per B.S.S. 497.  Manhole steps shall be of mild steel

3. 	APPLICABLE SECTIONS OF SPECIFICATIONS

The following specification sections shall be followed for carrying-out civil works associated with this section.

S.NO.    	Section

1.     	 	Earthwork

2.      		Formwork

3.      		Reinforcement

4.  		Plain and Reinforced Concrete

5.      		Brick Masonry

6.      		Plumbing

7.      		Manhole covers, road gully gratings and frames for drainage purposes

4. 	CONSTRUCTION

Manholes, Valves chamber or Grease trap etc. shall be of Reinforced Cement Concrete/Brick Masonry of the sizes, thickness and class of concrete as shown on the applicable drawings. Where soil is alkaline sulfate resistant cement shall be used for concrete work.  The work of excavation, backfilling, disposal of surplus/rejected earth, plain and reinforced cement concrete, Formwork, reinforcement, benching, pipe connections and provision and installation of C.I. cover with frame, ladder rungs, valves etc., are to be done under this section and shall be executed in accordance with the specifications as stated above.  C.I. frames, valves and ladder rungs shall be well set in place at the time of pouring concrete.

All mortar shall be used within 40 minutes after mixing. Mortar, which has begun to take on initial set, shall be discarded and shall not be mixed with additional cement or new cement.

Manhole inverts shall be constructed of concrete conforming to the requirements of section 2300 with exception that the concrete shall have minimum 28-day strength of 3000psi.

In no case shall the invert section through a manhole be greater than that of the outgoing pipe. The shape of the invert shall conform exactly to the lower half of the pipe it connects. Side connections shall be connected with as large radius curve as possible. All inverts shall be troweled to a smooth clean surface.

All manholes under construction shall be covered in an appropriate manner to prevent the entry of any storm water run-off, trench water, sand, earth or any other foreign substances at any time during construction or while the manhole is unattended.

Manholes/valve chambers shall be constructed with brick masonry laid in 1:3 cement sand mortar, built on class `D' concrete base slab.  The cover slab shall be Class `C' reinforced cement concrete, fitted with cast iron frame which shall have reinforced cement concrete cover as shown in the drawings, the concrete shall be of Class `B'. Reinforcement and concrete shall conform to the requirements of Section "CONCRETE".  The outside and inside of the walls shall be plastered (1/2 inch thick) with 1:3 cement sand mortar and two coats of hot PB-4 bitumen shall be applied outside.

At the bottom of manholes for sewers, a proper channel as per Drawings, shall be constructed in the whole length of the manhole along the centerline of the sewers, to lead the sewage from one sewer to the other. Mild steel steps shall be installed at 12 inches interval inside the manhole during the construction of the manhole walls.  Cutting holes into the wall for the steps after construction will not be permitted. Top rung shall be 18 inches below the manhole cover and the lowest not more than 12 inches above the benching (floor).

Depth of manhole shall be from invert level of sewer to the top of manhole

  - CONCRETE MANHOLE SECTIONS

Manhole bases shall be pre-cast or cast-in-place reinforced concrete, set on a firm foundation.  Flow channels and benches shall be shaped with concrete.

Riser and base sections shall have cast or augured cut-outs of the required diameter for connections and outlet pipes; maximum size of cut-outs shall be equal to the outside pipe diameter plus four (4) inches.  A clearance of at least nine (9) inches of concrete shall remain between adjacent connection and outlet pipe holes and between riser joints and holes in pre-cast risers and bases.  Lesser clearance will be considered only if additional reinforcing steel is provided and details are submitted for approval

For manholes on sanitary and combined flow sewers 24 inches and smaller diameter, the Contractor shall install a lubricated, rubber gasket entry seal into the manhole wall to effect a watertight connection between the connecting sewer pipe and the manhole.

Entry pipe shall be cut flush with the inside wall of the manhole.

Manhole risers shall be constructed of pre-cast concrete elements where feasible, otherwise of brick masonry.  Risers and cone tops shall be furnished with manhole steps 12 inches on center.  Manhole steps shall be aligned on vertical section of sidewall having no pipe entry, with step legs embedded 3-3/8 inches into the concrete.

  - CIRCULAR BRICK MANHOLE SECTIONS

Manhole brickwork shall be plumb except for the eccentric top section, true to line with level and accurately spaced courses, with each course breaking joint with the course below.  Joints shall not be less than 3/8 inch nor more than ½ inch with a minimum of one header course to every six (6) stretcher courses.  Each brick shall be placed with a full joint in a full bed of mortar, shoved up against adjacent brick so that the mortar rises between and completely fills vertical joint.  Exterior surfaces of brick manholes shall be completely coated with a ½ inch mortar parging and made watertight.  Brick Masonry wall shall be nine (9) inches thick; thickness shall be increased to 13.5 inches when manhole depth exceeds 8 feet.

Brick masonry shall not be placed when the ambient air temperature is below 40 deg.  F and when it appears probable that temperatures below 40 deg.  F will be encountered before mortar can set, unless adequate approved means are provided for protecting the work from freezing.  Work shall be protected by heating and maintaining the temperature of the masonry materials at not less than 40 deg.  F. on both sides of the masonry for not less than 72 hours.  Work with, or on, a frozen material is prohibited.

During hot weather, masonry shall be protected from direct rays of the sun.  All finished work shall be covered and kept damp for a period of seven days after placement.

Mortar shall be freshly mixed for prompt use; no mortar shall be used after setting or beyond 40 minutes after the addition of water.  Re-tempered mortar and freeze preventive chemical additives are prohibited.  The mixing machine, batch size, and mixing time shall be approved by the Engineer.  When hand mixing is done, mixing shall be accomplished in a clean, leak proof, nonporous mortar box constructed for the purpose.

Proper size manhole steps shall be aligned on section of side wall that is vertical to frame and cover, with step legs embedded 7-3/8 inches into the brick work.

The Contractor shall furnish manhole frames drilled with two 3/4 inches diameter holes, 180 degrees opposed in frame flange.  With frame in proper position at required grade, corresponding holes shall be drilled with a minimum of two (2) inches into the brick masonry upon which the frame sits.  Steel dowels shall be inserted through these holes to prevent lateral movement of frames during backfill and paving operations.  Dowels shall be No. 5 re-bars, three (3) inches minimum length, or approved equivalent.  A mortar bed shall be constructed around the frame flange.

  - COMBINED CONCRETE/BRICK SECTIONS.

Where approved by the Engineer, manholes may be constructed from a combination of brick masonry, and cast in place reinforced concrete.  Aft the point where the different materials join, a watertight joint shall be provided that leaves interior walls straight and smooth.

- DAMP-PROOFING

Surfaces to receive damp-proof material shall be dry. Before backfilling is started, the exterior surfaces of manholes shall be painted with two heavy coats of coal tar paint.

- STUBLINES

Stub-lines for future connections shall be provided in manholes at the locations indicated on drawings and shall terminate in a bell and plug.

- COVERS

Covers shall be set and securely fastened in place with concrete. The covers for sewer manholes shall be set at levels designated by the Engineer; but in general shall be as follows:

- In paved areas, the cover shall be 1/8 to 1/4 inch above the surface of surrounding pavement.

- In graveled traffic ways or parking, the cover shall be set from 1/4 to 3/4 inch above surrounding surface.

- In traffic ways of un-surfaced streets, the covers shall be set approximately level with the ground surface.

- In grassed areas and the un-traveled portions of streets, the covers shall be set from 1 to 2 inches above the surface.

- In ditches or other drainage ways, the covers shall be set high enough to be above the water in rainstorms.

- MANHOLE STEPS

Mild steel steps (ladder rungs) of ¾” diameter shall be built into the walls of manhole bases as shown on drawings, with legs embedded at least 3-3/8 inches into the concrete and at least 7-3/8 inches into the brickwork. First i.e. topmost step shall be 18” below the top of manhole. Intermediate steps shall be placed @ 12” c/c, while the lowermost step shall be maximum 2’-0” above the invert of manhole.

9. 	MEASUREMENTS AND PAYMENT

9.1	MEASUREMENT

Measurement of acceptably complete works of manhole, valves chamber etc., will be made on the basis of actual quantities  of different components of manholes, valve chambers or Grease trap etc., constructed and installed in position as specified herein, as shown on the drawings and/or as   directed by the Engineer.

9.2    	PAYMENT

Payment will be made for acceptable actual measured quantities of different components of manholes; valve chamber etc., on the basis of unit rate quoted in the relevant   items   Bills of Quantities and shall   constitute   full compensation for the works related to the item.