SECTION - 5311

SEWER PIPES, PIPE LAYING AND APPURTENANCES

1		SCOPE

2		MATERIALS

- CLASSES OF PIPE

- BASIS OF ACCEPTAVNCE

- PIPE DIMENSIONS

- CERTIFIED DRAWINGS AND DATA SHEETS

- JOINTS FOR CONCRETE PIPE SEWER

- HOUSE CONNECTIONS

- INSTALLATION

- TESTING OF SEWER LINES

- MEASUREMENT AND PAYMENT

SEWER PIPES, PIPE LAYING AND APPURTENANCES

1	 SCOPE

The work covered by this section of the specifications consists in furnishing all reinforced concrete pipes, plant, labour, equipment, appliances and materials and in performing all operations required for installing and testing the sewer pipes in strict accordance with the specifications of this section and the applicable drawings and subject to the terms and conditions of the contract.

2	MATERIALS

All materials used in the manufacture of reinforced cement concrete pipes for use under this contract shall conform to ASTM Designation C-76 or latest revision and also with the following specifications. Plain cement concrete pipe shall conform to ASTM designation C-14, latest revision.

01	Cement

The portland cement to be used in the manufacture of reinforced concrete pipes shall conform to the requirement of ASTM Designation C 150 (latest revision).

02 	Aggregates

The coarse/fine aggregate to be used in the manufacture of concrete pipes to be furnished and installed under this contract shall be generally in accordance with the provisions of Section 2300 of these specifications.

03	Water

Water to be used in the manufacture of pipes shall be approved by the Engineer.

- Steel Reinforcement

The material shall conform to the specifications contained in respective section of specifications.

05 	Brick Ballast

Brick ballast shall have a maximum gauge of 1 1/2 inch and shall be graded down to 3/4 inch and shall not contain more than 10% which will pass through screen made of 1/4 in. diameter bars spaced at 3/4 in. centre to centre.

3	CLASSES OF PIPE

The reinforced cement concrete pipes to be furnished and installed under this contract shall be of the strength Class II or specified otherwise on the Drawings.

Following technical criteria shall be adhered to:

Class of Pipe		:	Class II

Concrete Strength	:	4000 Psi (Cylinder Test)

The design requirements for these classes of reinforced cement concrete pipes shall be as described in ASTM Designation C-76, Table 1 to 5 for the respective strength classes. Unless otherwise called for in other parts of these Technical Specifications or applicable variation order, all reinforced cement concrete pipes under this contract shall comply with the Wall B design requirements as set forth in said Table 1 to 5 of ASTM Designation C-76 or latest revision.

4	BASIS OF ACCEPTANCE

Acceptance of reinforced cement concrete pipes will be on the basis of three edge bearing and material tests as per ASTM Designation C-76 or latest revision and inspection of manufactured pipes for defects and imperfections. The Contractor shall bear the cost of such tests and pay fees etc., and also pay for the carriage of such samples and all other expenses contingent to tests.

5	PIPE DIMENSIONS

The internal diameters and wall thickness of reinforced concrete pipes under this contract shall be as set forth in ASTM Designation C-76 or latest revision in Tables 1 to 5 for "Wall B" pipes as required and shown on the Drawings.

The lengths of reinforced concrete pipes under this contract shall be as required to provide the designated laying length plus any overlap needed for the pipe joint. Pipe shall be of standard length of 8 ft. unless otherwise approved in writing by the Engineer. Only one laying length shall be permitted for each size of reinforced concrete pipe under this contract and pipes different than the approved uniform laying length shall not be used in the work.

For 9" dia R.C.C. pipes following data in addition to ASTM-76 shall be applicable.

-	Wall thickness				 1"

-	Reinforcement square inches

per linear foot of pipe wall 0.05

-	Concrete strength			4000 Psi												(cylinder test)

-	Inside diameter at the

mouth of socket				 12 1/2"

-	Depth of socket				 2 1/4"

Longitudinal Steel

Each layer of circumferential reinforcement shall be assembled into a rigid case supported by 4 Nos. longitudinal bar of quarter inch diameter.

-	The pipes shall be supplied in length of 8 feet. No variation in the length will be permitted without the written approval of the Engineer's Representative.

The strength test requirements in pounds per linear foot of pipe under the three-edge-bearing method shall be either the D-Load (test load expressed in pounds per linear foot per foot of diameter) to produce 0.01 in crack, or D-loads to produce the 0.01 in crack and the ultimate load as specified below, multiplied by the internal diameter of the pipe in ft.

D-Load to produce a 0.01 in crack 	= 	1000 pounds

D-Load to produce the ultimate load 	= 	1500 pounds

Lift holes in the walls of reinforced cement concrete pipes will not be permitted under this contract for the purpose of handling and laying. Other approved lifting methods shall be employed.

6	CERTIFIED DRAWINGS AND DATA SHEETS

The Contractor shall submit in triplicate, for approval by the Engineer certified drawings and data sheets as required to provide complete information on all concrete sewer pipes, dimensions, type and dimensions of pipe ends, joint details, proposed concrete design mix for each different strength class of reinforced pipe and any other information needed to demonstrate full compliance with these specifications.

No concrete sewer pipe shall be delivered to the work site until the Engineer has formally approved the certified drawings and data sheets and until all test requirements called for in the respective ASTM Standard Specifications C-76 or latest revision have been met.

7	JOINTS FOR CONCRETE PIPE (SEWERS)

Rubber gasket joints shall be used for either tongue and groove or bell and spigot pipes.

Rubber gasket joints shall be made using specially designed rubber gaskets, made to fit the applicable tongue and groove or bell and spigot pipes and adequately tested under operating conditions. Special care must be taken in the selection and handling of the concrete pipes for use with rubber gasket joints, to ensure that pipe ends shall be smooth and concentric with tolerance which closely conform to the requirements of the manufacturer of the rubber gaskets. The tongue orspigot end of each pipe shall be specially designed to perform groove or offsets to fit the manufacturer's rubber gaskets design.

The rubber gasket joints shall conform to all applicable requirements of the latest revision of ASTM Designation C443, entitled "Joints for Circular Concrete Sewer and Culvert pipe, using Flexible Watertight Rubber Type Gaskets" except that the test pressure need not exceed 10 feet of head at which the complete sewers shall meet the infiltration or exfilteration limits set forth hereinafter.

The groove end of tongue and groove pipes shall have at least one line of wire reinforcement of 8 gauge size placed in the centre of the groove.

The rubber gasket shall be installed on the pipe in accordance with the instructions of the gasket manufacturer. In general the gaskets shall be pre-assembled to the pipe at the pipe manufacturing plant. The pipes shall be handled with special care at all times to prevent damage to the pipe ends. A lubricant shall be used for jointing the pipes as recommended by the rubber gasket manufacturer. Care shall be taken to avoid contamination of the gasket and lubricated surfaces with earth or other undesirable material during installation.

For either tongue and groove or bell and spigot pipes, mechanical means shall be used to pull the pipe home for all sizes of 12" or larger diameter in accordance with the recommendations of the rubber gasket manufacturer. Pipes of 9 inches diameter may be coupled manually using a cross member and bar. Under no circumstances will bars alone be used nor shall any motor driven equipment be used to force the pipe home.

8	HOUSE CONNECTIONS

House Connections shall be made through manholes as indicated in the drawings or as directed by the Engineer.

House connection shall be provided individually for each plot by means of a 6" dia R.C.C. sewer pipe and a dead end, laid at an average depth of 3.5 feet below N.S.L. level and in such a manner that other services such as water supply, telephone and gas lines are not disturbed or interfered. The work of laying the sewer pipe shall conform to the specifications laid down in the relevant section of this contract.

The inlet of each house connection shall be plugged with brick masonry 4 1/2 inch thick in 1:6 cement sand mortar both in the manhole and the pipe in the plot.

9	INSTALLATION

01	Handling of Pipes

Concrete sewer pipes shall be handled with special care at all times during the manufacture, while transporting to the site of work, and while installing. Each pipe shall be carefully inspected before being laid and no cracked, broken or defective pipe shall be used in the work. Chipping of the tongue and groove or bell and spigot pipe ends, which in the Engineer's opinion may cause defective joints, shall be sufficient cause for the rejection of any concrete pipe.

02	Excavation and Backfill

The excavation and backfill for sewer installations shall be as specified in applicable provisions of these technical specifications and will be paid for under separate contract items as classified or and as per applicable variation orders.

03	Placing of Bedding

a)	Sand Bedding

US Standard Sieve size			 % passing

3/8 in. (9.5 mm)				 100

No. 200 (0.075 mm)			 0-5

The sand shall be clean material obtained from approved source. Sand shall be well graded, perfectly clean, free from coagulated lumps, soft and flaky particles, shale, alkali, organic matter loam, mica and injurious amount of other deleterious substances.

The material shall be evenly spread over the full width of the formation in 4 inches loose layers and compacted with hand or mechanical remmers untill the full thickness as shown on drawings for the particular pipe size has been built up and finished not more than 1/2" below required level. The Contractor shall note that it is essential that the material at the sides of the pipes is adequately compacted. Before the subsequent placing of pipe surrounding material, pipe joints shall be protected. Protection may take the form of a twist of yarn lightly pressed into the annular joints space or other equal protection approved by the Engineer's Representative.

b) 	Brick Ballast Bedding

The brick ballast shall be clean material of 1 to 1 1/2 inch gauge broken from first class bricks or bats, or from dense over burnt bricks. No under-burnt bricks or bats nor those which have become spongy or porous in the process of burning shall be broken up for brick ballast.

The material shall be evenly spread over the full width of the formation in 4 inches loose layers and compacted with hand or mechanical rammers until the full thickness as shown on the drawings for the particular pipe size has been built up and finished not more than 1/2" below required level. The Contractor shall note that it is essential that the material at the sides of the pipes is adequately compacted. Before the subsequent placing of pipe surrounding material, pipe joints shall be protected. Protection may take the form of a twist of yarn lightly pressed into the annular joints space or other equal protection approved by the Engineer's Representative.

c)	Crushed Stone Bedding

Crushed stone bedding shall be from an approved source. It shall be obtained from a dark coloured igneous rock such as granite etc. It shall be strong, durable, hard and impervious, having crystalline structure. The broken stone shall have sharp edges and clear fractured faces, shall be free from thin elongated or laminated pieces.

The crushed stone shall have a maximum gauge of 1 1/2" and shall be graded down to 3/4". When shifted through a screen made of 1/4" diameter bars spaced 3/4" center to center, it shall yield no more than 10 percent by volume of fine materials.

04	Laying of Sewers

Neither any sewer pipe nor the bedding shall be laid or placed till the alignment of the sewer and its levels and gradients have been carefully checked and tested with the trench excavation and found correct.

Each length of sewer pipe shall be checked for cracks and defects before placing in the line. Defects which in the opinion of the Engineer indicate imperfect placing, shall make, the pipe liable to rejection. Each pipe shall be placed carefully to line and grade and in close contact with adjoining pipe. These specifications require rejection of the work if the sewer invert varies as much 1/2 inch from the proper elevation. As shown on drawings, the bottom of the trench must be shaped to fit the pipe barrel, with holes left for the bells. If excavation has been carried below the correct grade, refilling must be done with satisfactory materials as approved by the Engineer at no extra cost. The concrete pipe joints shall be of the type specified above and shall be made in accordance with the aforesaid specifications.

When laying is not in progress, the open pipe shall be closed with a tapered wooden plug to keep out foreign matter.

05	Pavement Restoration

The Contractor shall restore paved surface which have been cut under this contract, as part of the work under the Excavation items and at no extra cost of the Owner.

10	TESTING OF SEWER LINES

01	General

All sewer built under this contract shall be tested for infiltration or exfiltration as specified below. The tests shall be made at times selected or approved by the Engineer. Sections of the completed sewer shall be isolated and measurements of the infiltration or exfiltration shall be made by approved method. The contractor shall furnish all labour, material and equipment required for making the tests with no extra compensation over and above the agreed contract prices for the laying of sewer lines.

02	Infiltration Tests

The sewers which are constructed with the ground water level above the invert level of the pipe shall be tested for infiltration after the sewers have been installed and backfilling has been substantially completed. The tests and measurement shall be performed by the Contractor in the presence of and in a manner approved by the Engineer. The duration of the tests shall be only long enough to establish the true rate of infiltration. The amount of leakage over a 24 hour period will then be calculated from the result of the measured true rate of infiltration.

03	Exfiltration Tests

The sewers which are constructed with the ground water level below the invert level of the pipe shall be tested for exfiltration by isolating a section of sewers between manholes by means of approved temporary type of water tight bulk heads. The method of testing for exfiltration shall be generally as follows:

- After isolation of sewer section, it shall be filled with water to a level which is 3' above the crown of the pipe at the higher end of the isolated section under test. The level will not be more than 6 ft. above the invert level of the sewer pipe at its lower end.

- The duration of the exfiltration test shall be one hour after the filling with water has been completed.

- Determination of the amount of exfiltration shall be made by measuring the total loss of volume of water in the manholes.

- The amount of exfiltration over a 24 hour period will then be calculated from the measured loss of volume during the test observation period.

04	Allowable Infiltration or Exfiltration

The calculated amount of infiltration or exfiltration over a 24 hour period shall not exceed 500 gallons per inch of pipe diameter per mile of sewer which rate shall be applied to the actual sewer size and length tested to determine the allowable infiltration or exfiltration over the 24 hour period.

If the measured infiltration or exfiltration exceeds the specified allowable limit, then the Contractor shall locate the points of leakage and make necessary repairs so as to reduce the leakage to less than the permissible maximum stated above.

05	Cleaning of Sewer Lines

The contractor shall clean all the sewer lines at no extra cost with the method approved by the site Engineer prior to handing it over to the Owner.

11	MEASUREMENT AND PAYMENTS

Measurement and payment for sanitary sewers will be made in accordance with the provisions given hereafter.

01	Bedding

a)	Method of Measurement

The quantity to be paid for under this item will be the number of cubic feet of bedding material acceptably placed under sewers complete in all respects as per relevant drawings.

b)	Basis of Payment

Payment shall be made for the number of cubic feet of bedding material measured as provided above at the Contract Unit Price per cubic foot and shall constitute full compensation for all work related to the item.

02	Sewers

a)	Method of Measurement

Measurement shall be made at site of the actual lengths of reinforced concrete pipes of different sizes and strength installed and tested, as authorized for payment under this contract. The measurement will be made along the centre line of the pipe and between the inside walls of manholes or junction chambers. The unit of measurement will be linear feet.

b)	Basis of Payment

The unit rate quoted in the priced B.O.Q. for supplying, laying and joining cement concrete sewerage pipes shall include full compensation for the cost of pipes, charges for their carriage to site and testing before and after laying, labour charges for laying, jointing, cleaning of sewer lines etc. and cost of all incidentals for completion of this item of work as per specifications laid down in this section.

03	House Connections

a)	Method of Measurement

Measurement shall be made at site of the actual length of 6" dia reinforced concrete pipes installed and tested, as authorized for payment under this contract. The measurement will be made along the centre line of the pipe and between the inside walls of manholes or junction chambers. The unit of measurement will be linear feet.

b)	Basis of Payments

Payment will be made for the L.ft of 6" dia R.C.C. Pipes as measured above at the contract unit price per linear ft. and will constitute full compensation to supply, lay and joint 6" dia R.C.C. Pipe for house connection including testing and all other works related to complete the item in accordance with lines and grades as shown in the drawings or as directed by the Engineer.