SECTION - 5150

FIRE PROTECTION

- SCOPE

- APPLICABLE STANDARDS

- SUBMITTALS

- MATERIAL

- DELIVERY AND STORAGE

- EXECUTION

- TESTING & COMMISSIONING

- MEASUREMENT AND PAYMENT

1. 	SCOPE OF WORK

The work to be done under this section of the Specifications includes furnishing all plant, labour, equipment, appliances and materials and in performing all operations required in connection with the supply and installation of galvanized steel pipes and fittings for fire fighting system, portable fire extinguishers, fire hose rack cabinets and landing valves as shown on the Drawings, as specified herein and/or as directed by the Engineer.

2. 	APPLICABLE STANDARDS

# Portable Fire Extinguishers		BS- 5423

Portable fire extinguishers shall conform to NFPA (National Fire Protection Association) of USA or F.O.C. (Fire Offices Committee) of U.K. and B.S. 5423.

- SUBMITTALS

The contractor shall submit technical brochures and samples of all the items mentioned in the Specifications from approved manufactures or as directed by the Engineer.

4.	MATERIAL

4.1	PORTABLE FIRE EXTINGUISHERS

Portable fire extinguishers shall contain specified quantities and types of extinguishing agents. Extinguishers shall be classified according to type of extinguishing agents and the Class of fire types for which it is intended to be used. The extinguisher container/vessel shall be of anticorrosive material or otherwise lined internally with corrosion-resistant material. The outside surfaces of the container/vessel shall be painted with at least two coats of anti-corrosive paint.

The extinguisher container shall be designed as pressure vessel and shall conform to all the applicable standards of ASME pressure vessel codes.

The container shall be fitted with spring-loaded pressure safety valve. The valve shall be set to blow off at 90% of container test pressure.

4.1.1 	Dry Chemical Extinguisher

Dry chemical extinguisher shall contain specified quantities of dry powder chemical. The type of dry powder shall be suitable for the intended use.  The extinguisher shall have knob or lever operated valve, a short length of hose and a nozzle at the end of the hose. A siphon/dip tube shall extend from the valve to the bottom of the container. The valve shall have safety pin to prevent accidental release of the extinguishing agent. The discharge pressure shall be obtained from pressurized carbon dioxide cartage attached to the body of the extinguisher. The operation of the knob or lever shall pierce the cartage to obtain the expellant pressures. When operated the discharge time of 10 lbs. dry powder extinguisher shall not be less than 9 seconds.

4.2 	FIRE HOSE CABINET

Fire Hose Cabinet shall consist of rubber hose of specified diameter and length as shown on the applicable drawings. The hose shall have polished brass valved nozzle at one end. The reel shall turn full 180 degrees. Hose and reel shall be placed in a steel or concrete fire box with glazed steel door. The door shall open full 180 degrees and shall be provided with locking arrangement. The locking arrangement will be such that the cabinet can be opened either by breaking the front glass and turning the handle from inside or with key from outside without breaking the front glass.

The exposed front face of fire hose cabinet shall be painted with signal red enamel paint over a prime coat of anti-corrosive paint. Instructions for opening of fire hose cabinets and operation of hose reel shall be inscribed in signal red on the inside face of the glass such that the instructions can be read from outside.

The hose shall be rated for a working pressure of 16 kg/cm2 and test pressure of 25 kg/cm2.

- DELIVERY & STORAGE

Portable fire extinguishers shall be delivered and stored as per manufacturers directions or as directed by the Engineer while observing all necessary precautions.

6. 	EXECUTION

    - PORTABLE FIRE EXTINGUISHERS

Portable fire extinguishers shall be installed at one meter height above finished floor.

Where only extinguishers are installed they shall be fixed to wall or column with painted steel clamps or stored in steel or concrete fire extinguisher cabinets as shown on the applicable drawings or as directed by the Engineer. Where clamped to the wall/column the clamp shall be such that extinguisher can be conveniently fixed and removed without loss of time.

Where stored in cabinets, the cabinets shall be of steel or concrete with glazed steel door painted with at least two coats of anti-corrosive signal red enamel paint over a prime coat of red oxide paint. The locking arrangement will be such that the door can be opened from inside by breaking the glass and from outside with key.

#### Markings

Portable Fire extinguishers shall be painted with color code according to British Standard specifications. On the body of the extinguishers shall be marked/imprinted the following information.

a) 	Instructions on how to use the extinguisher.

b) 	Name of the extinguishing agent.

c) 	Weight/volume of the extinguishing agent.

d) 	Gross weight of the extinguisher.

e) 	Filling pressure of the extinguishing agent.

f) 	Classes of fires for which the extinguishing agents may be effectively used.

g) 	Name of the manufacturer and the year of manufacture.

h) 	Validity/ expiry date

    - Fire Hose cabinet

Fire Hose Cabinet shall be installed at one meter height above finished floor level. The fire hose shall be connected to fire/or potable water system as the case may be, through a Hydrant valve. The valve shall be rated for a working pressure of 16 kg/cm2.

If the pressure at the valve exceeds 6 kg/cm2 then an orifice plate shall be installed between the gate valve and the fire hose so that the water pressure in the hose shall not exceed 6 kg/cm2 under any condition.

7. 	TESTING & COMMISSIONING

The fire water line shall be tested at 1.5 times the working pressure.

8. 	MEASUREMENT AND PAYMENT

8.1 	FIRE HOSE CABINET

8.1.1	Measurement

Measurement of acceptably completed works of fire hose cabinet will be made on the basis of actual number of fire hose cabinet provided and installed in position as shown on the drawing or as directed by the Engineer.

8.1.2 	Payment

Payment will be made for acceptable measured quantity of fire hose cabinet on the basis of unit rate per number quoted in the Bill of Quantities and shall constitute full compensation for all the works related to the item.

8.3	PORTABLE FIRE EXTINGUISHERS

8.3.1 	Measurement

Measurement of acceptable completed works of portable fire extinguishers will be made on the basis of actual number of extinguisher provided and installed in accordance with the above specifications and applicable drawings.

8.3.2 	Payment

Payment for acceptable measured quantities of portable fire extinguishers will be made on the basis of unit rate per number quoted in the Bill of Quantities and shall constitute full compensation for all the works related to the item.