SECTION - 8150

LIGHT FIXTURES

1.0	SCOPE OF WORK

The work under this section consists of supplying, installing, testing and commissioning of all material and accessories of the complete Light fixtures as specified herein and/or shown on the drawings and given in the Bill of Quantities.

The Contractor shall discuss the electrical layout with the Engineer and co-ordinate at Site with other services for exact locations and positions of the light fixtures.

The lighting fixtures with accessories shall also comply with the General Specifications for Electrical Works, Section-8001 and with other relevant provisions of the Tender Document.

2.0	GENERAL

The description of light fixtures is given in the bill of quantities, and stated on the drawings, and all relevant material is described in this Section.  The determination of quality is based on certified photometric data covering the coefficient of utilization, light distribution curves, construction material, shape, finish, operation, etc.

The Contractor shall submit the samples of each and every light fixture specified and obtain approval of the Engineer before purchasing. The quality and finishes of the local make light fixtures (if mentioned in BOQ) shall be same as that of standard manufacturer. The accessories such as ballast, lamp/starter holders, starters, lamps, ignitors, etc.  for all type of light fixtures shall  be  of Philips  make  or approved equivalent. Approved equivalent against those specified will be accepted if the specified one is/will not be available. For any substitution the Engineer's approval is necessary.

All fixtures shall be finished in standard color schemes as mentioned in the manufacturer's catalogue for respective fixtures, unless specifically stated in the Specifications, Drawings or Bill of Quantities or directed by the Engineer.

3.0	APPLICABLE STANDARDS/CODES

The latest editions of the following standards/codes shall be applicable to the material specified within the scope of this section:

IEC 81 & BS 1853	- 	Tubular fluorescent lamps

IEC 82 & BS 2818	- 	Ballast for tubular fluorescent lamps

IEC 155 & BS 3772	- 	Starters for fluorescent lamps

IEC 400	- 	Lamp holders and starter holders for fluorescent lamps

IEC 1048, 566, 1049	- 	Capacitors for use in TL, HP Mercury and LP Sodium Vapour Lamps.

BS 3677/3767/4017 	- 	Discharge Lamp Circuits

IEC 598

IEC 922/923	-    Luminaires

BS 5266	-	Emergency Lighting

BS 2560    	-  	Exit Signs

4.0	MATERIAL

4.1	Fluorescent Light Fixtures

The fluorescent light fixtures shall have lamps and ballasts of proper rating as shown on the drawings.  Each 36 W lamp shall be provided with independent ballast.

The fluorescent lamps shall be tubular, 1214/604mm long, 28-mm. dia. for 36/18 watts respectively as specified. The fluorescent shall be cool white, with colour rendering and light colour of 840 characteristics with an average output  of  3350  lumens  (+ 5%)  for  36  watts  and  1350  lumens  (+5%) for 18 watts after 100 burning hours.  The ballast shall be ‘Low Loss’ polyester  filled  type,  totally  enclosed  and  suitable  to  operate  upto  250 VAC. The power loss shall not be more than 6 watts for 36/18 watts ballast. A wiring diagram, wattage, voltage and current figures shall be printed on the body of the ballast.

The lamp holders shall be rotary lock-in type. The starters shall be glow type with radio interference suppressor/by-pass capacitor. The internal wiring of the fluorescent light fixtures shall be done with heat resistant wires at the manufacturer's factory. The internal wiring shall be clipped properly and heat resistant sleeves be provided on cables passing near ballasts. All light fixtures shall be provided with power factor improvement capacitor to give a minimum power factor of 0.90.  Connectors suitable for connecting 2.5 sq.mm cable conductors shall be provided for supply connections. An earth terminal for connection to 2.5-sq.mm cable conductor shall be provided.

The body of the fluorescent light fixtures shall be minimum 24 SWG sheet steel, derusted, degreased, finished in heat resistant paint, stove enameled. Appropriate size bushed wire entry holes, fixing holes, and earth terminal shall be provided.

The light fixtures shall be furnished with Perspex diffusing panels "040 opal acrylic"  (minimum sheet thickness 3mm), polystrene louvers or metal grid louvers or mirror optic reflectors, etc.  as specified on the drawings or in  BOQ. The louvers shall be secured firmly and in level. The louvers shall be in one section and not in pieces.

The design of light fixture for recess mounting shall be coordinated with the design of false ceiling prior to commencement of manufacture. Shop drawings shall be submitted for approval of Engineer.

IP degree of protection shall comply with the requirements laid down in section 8001. Standard luminaires with manufacturer’s recommended modifications, such as, additional gasket, etc. shall be provided to attain required protection level.

4.2	Incandescent / Incandescent reflector/

compact fluorescent Light Fixtures

The incandescent/incandescent reflector/compact fluorescent light fixtures shall be as stated on drawings and bill of quantities. The light fixture shall be finished in standard colours unless otherwise stated on drawings or directed by Engineer. All incandescent/incandescent reflector/compact fluorescent light fixtures shall be of international standard and quality. The types of fixtures with manufacturer’s catalogue reference are given on the fixture schedule and in bill of quantities. Equivalent fixture may be acceptable provided that the contractor submits for review all necessary data indicating photometric curves to show that the fixture proposed are of the same type, construction and quality.

The lamps for incandescent/incandescent reflector/compact fluorescent light fixtures shall be GLS lamps or incandescent reflector (PAR) or compact fluorescent lamp with normal or electronic control gear and shall be supplied and installed according to the wattage/type as indicated on drawings.

Weatherproof bulkhead incandescent/compact fluorescent light fixture shall comprise of  plastic body and gasketted clear glass cover secured to the body by means of wing nuts/screws to give a weatherproof and watertight fit. The gasket shall be weather resistance type. The lamp holder shall be of bi-pin brass having porcelain outer ring or 2/4-pin base for compact fluorescent lamps with normal control gear as per requirements.

The glass shade of the light fixtures shall be opal white or clear as furnished by the manufacturer with the light fixture unless specified and free from any air bubbles or voids. The shade may be spherical, cylindrical, flattened bottom or any other shape as specified in the drawings or BOQ.

4.3	High / Low Bay Light Fixture

The industrial type mercury light fixture shall consist of circular reflector of anodized aluminum providing bare lamp cut-off at an angle of 62o to the vertical, glass cover and gasket. The reflector shall have aluminium canopy having ¾” (19mm) threaded hole for  fixing on the bracket. The lamp holder shall be of porcelain and wired to the mains terminals with heat resistant wires. The fixture shall be provided with mercury vapour lamp of 400 or 250 watts, with appropriately rated ballast, power factor correction capacitor and have terminals provided for connecting to minimum size of 4 sq.mm single core wires. The ballast to be housed in the choke box provided integral with the fixture.

4.4	Road Light Fixtures

The road light fixture shall be high performance lantern for high pressure sodium lamp. It shall be suitable for low threshold increment distribution to BS 5489-2. The fixture shall have white glass reinforced polyester canopy with seamless polyurethane gasket, high purity anodized aluminium reflector and toughened glass lens with stainless steel hinges and toggles. The integral control gear shall be mounted on pressure die cast aluminium alloy end support. The fixture shall have side entry with suitable fixing arrangement for G.I. pipe bracket. The fixture shall conform to IP 66 protection Class.

The lamp for road light fixture shall be increased output high pressure sodium lamp (SON-T). The lamp wattage shall be as shown on the drawing.

The control gear hall have ballast, igniter and power factor correction capacitor. The ballast power loss shall not be more 32 watts for 400 W SON-T lamp.

4.5	Under Water Flood Lights for Fountains

The under water flood lights shall have lamps of ratings specified in BOQ/ Drawings and shall be equipped with proper rating control gears, etc., complete with internal wiring and suitable cable tail (5 m or as required) up to transformer.

The transformers for underwater lights shall be compatible with light fixture, and shall be of same make as that of light fixtures.

The fixtures and accessories shall be manufactured to comply with EN 60598. Floodlights shall be dusted jet proof to IP 68 and suitable for installation at a depth of at least 5 m under meter. The transformers shall be rated to IP 54.

The body of the fixture shall be of copper alloy construction employing PAR 38 120w/24 V or PAR 56 300 W/12V lamps, as required.

5 Nos. of spare gland seal and lamp O-ring shall be supplied with each light fixture.

4.6	Decorative Bollards

The decorative bollards shall have lamps of ratings specified in BOQ/drawings and shall be fully equipped with proper rating control gears, capacitor etc. complete with all internal wiring.

The bollards shall have UV-stabilized polycarbonate optical unit, polycarbonate diffuser, aluminium internal louvers (painted white) and appropriate gear tray, extruded PVC column/aluminium, cast aluminium bollard base and vandal resistant arrangements. The housing shall be dustproof and jet proof to IP54, such that no internal cleaning shall be required.

The colour of the bollards shall be as approved by the Engineer.

5.0	LIGHT FIXTURE INSTALLATION

5.1	General

The mounting heights of light fixtures are indicated on the drawings, and positions of fixtures are according to the mentioned scale.

The Contractor must ensure that the light fixtures are installed uniformly with respect to the dimensions of the area.  Any modifications due to site conditions may be made with the approval of Engineer. All fixtures shall be carefully aligned before fixing in position.

The wiring between ceiling rose or terminal box and the fixture shall be carried out with 3-core 1.0 sq.mm and 1.5-sq.mm flexible copper conductor PVC/PVC cable respectively for circuits protected by 10 amps and 15/20 amps mcbs. The wiring inside light fixture body shall be done with heat resistant cables or PVC insulated cable in heat resistant sleeves as approved by the Engineer.

Glasses, shades, reflectors, diffusers, etc., must be in a clear condition after installation. All light fixtures shall be earthed by an earth wire connected to the earth terminal in the fixture.

5.2	Fluorescent Light Fixtures

The fluorescent light fixtures on the surface of ceiling shall be installed with the back of the body flush with the ceiling surface, and in a manner so as to facilitate wiring. Nylon plugs and galvanized steel bolts or screws shall be used for fixing the light fixture to the ceiling. For light fixtures installation on false ceiling the installation method/detail shall be coordinated with ceiling design and submitted for approval of Engineer.  Care shall be taken to prevent the weight of the fixture from being transferred to the false ceiling.

Pendant light fixtures shall have two holes in the top of each casing for supporting to the ceiling by a 3/4" dia.  galvanized pipe  or any other standard method as approved by  the Engineer. Wiring from ceiling rose to the fixture shall be done through the pipe. Proper arrangements such as long threads with check nuts, etc. for minor adjustment in the mounting heights of the fixtures shall also be provided.

5.3	Incandescent/Incandescent reflector/

compact fluorescent Light Fixtures

The incandescent/incandescent reflector / compact fluorescent light fixture shall be installed on the surface of ceiling or wall by means of nylon plugs and galvanized steel screws, such that their back finish flush with the surface for exposed conduits and flush with outlet box for concealed conduit system.  Wherever convenient, screws for fixing light fixtures shall be screwed into the holes of the outlet box.  The lights on false ceiling shall be installed in a manner as described for fluorescent light fixture.

5.4	High / Low Bay Light Fixture

The high/low bay mercury vapour light fixture shall be installed in the roof surface/ trusses. Appropriate size and shape of steel clamps shall be fixing to the truss member for supporting the light fixture, and the light fixture shall be suspended to the required level with a steel rod. Rod length shall vary to keep the fixtures at a uniform level. The wiring between ceiling rose and fixture shall be with three core 1.5 sq.mm. PVC insulated PVC sheathed flexible cable.

5.5	Road Light Fixtures

The Road Light Fixtures shall be installed on G.I. bracket as per details shown on the drawing. Manufacturer’/s installation instructions shall be followed. The G.I. bracket shall be installed on column as shown on drawing.

5.6	Under Water Flood Lights for Fountain

The under water floodlights shall be installed as per finalized architectural layouts.

All mounting and fixing accessories shall be rust proof and suitable for installation under water.

The remote transformer shall be installed in purpose made UV protected transformer housing at a suitable place near fountain. The transformers shall be fixed with four lugs.

The conduiting inside fountain shall be done with rigid and flexible conduit. The installation shall ensure that water can not drip into transformer box (from conduit or out side).

5.7	Decorative Bollards

The bollards shall be three Allen Screws to a mounting flange with anchored bolt, cast in concrete base. Cable entry and exit through concrete foundation shall be done in suitable size class ‘D’ PVC pipe. Cable terminations shall be done with proper rating connectors suitable for connecting 6.0 sq.mm cables, looping in and out to other bollards. Cable armour and earth wire shall be connected/looped to all conductive parts of the bollard body.

6.0		MEASUREMENT AND PAYMENT

6.1	General

The Contractor's bid amount against each Bill of Quantities item as given below shall include supply, installation, testing, commissioning and completion for all work specified herein and/or shown on the Tender Drawings related to the item.

6.2	Fluorescent / Incandescent / Incandescent Reflector/

Compact Fluorescent / High/Low Bay & Road Light Fixtures

6.2.1  	Measurement:  Measurement  shall be made  for  each type of light fixture including all accessories acceptably supplied  and installed by the Contractor as complete unit.

6.2.2  	Payment: Payment shall be made for the number of units measured as provided above at the contract unit price each and    constitute full compensation for supplying, installing, connecting,   testing and completion of fluorescent/incandescent/incandescent reflector/compact fluorescent light fixture including all accessories such as ballasts, capacitors, igniters, lamps, lamp starter, holders, suspension rods, GI pipe bracket, ceiling supports, internal wiring, nuts, bolts, screws, etc., as required and complete in all respects.

6.3	Under Water Flood Lights for Fountain

6.3.1	Measurement:  Measurement shall be made for each type of underwater flood light for fountain including transformer, transformer housing including all accessories, foundation works etc., acceptably supplied and installed by the Contractor as a complete unit.

6.3.2	Payment:  Payment shall be made for the number of units measured as provided above at the Contract Unit Price each and shall constitute full compensation for supplying, installing, connecting, testing and commissioning of under water flood light, transformer, transformer pit, all accessories such as internal wiring, nuts, bolts, screws, etc. including PVC conduit, foundation etc., as required and complete in all respect.

6.4	Decorative Bollards

6.3.1	Measurement:  Measurement shall be made for each type of bollard including accessories, concrete foundation etc. acceptably supplied and installed by the Contractor as complete unit.

6.3.2	Payment:  Payment shall be made for the number of units measured as provided above at the contract unit price each and constitute full compensation for supplying, installing, connecting, testing and completion of bollards fixture, all accessories, such as internal wiring, nuts, bolts, screws, etc., including PVC pipe, foundation etc., as required and complete in all respects.