SECTION - 8212

LOW TENSION CABLES

1.0	SCOPE OF WORK

The work under this section consists of supplying, installing, testing and commissioning of all material and services of Low Tension (LT) Cables and the accessories as specified herein or as shown on the Tender Drawings and in the Bill of Quantities.

The Contractor shall discuss the electrical layout with the Engineer and coordinate at site with other services for exact route, location and position of the LT cables.

The LT cables with accessories shall also comply with the General Specifications  for Electrical Works, Section-8001 and with other relevant provisions of the Tender Document.

2.0	GENERAL

All multi-core and single core PVC insulated and sheathed cables for light circuits, socket outlets and circuits operating upto 250 volts shall be 300/500 volts grade.  All single core PVC insulated, non-sheathed cables shall be of 450/750-volt grade. Power cables for main feeders, main to sub main feeders, power equipment, etc., armoured or unarmoured shall be of 600/1000 volt grade. Armouring of multi-core/ single core cables shall be done with appropriate size galvanized steel/aluminium wire as per relevant codes.

The conductors shall be stranded high conductivity, soft annealed copper. Conductors of single core cables shall be circular, whereas of multi-core cables may be circular or shaped according to standard practices and codes. The PVC insulation, bedding and overall sheath shall be of extruded PVC compound having good flexibility, resistance to ageing and ability to withstand deformation at high temperatures. Non-hygroscopic filler shall be provided in multicore cable to fill empty gaps between the cores to make the cable a smooth round finish. In all shaped cables a non-hygroscopic high strength binding tape shall be provided on the core assembly. All cables shall be treated for vermin proofing and be protected against rodents during storage, laying and all protective pipe/sleeves shall be plugged to attain the same after installation.

Embossed marking on the oversheath at 3 meters intervals shall give the following information :

-	name of Manufacturer

-	year of  Manufacture

-	No. of cores and size of cable in sq.mm.

-	voltage grade

-	type of cable i.e. Cu./PVC/SWA/PVC

3.0    	APPLICABLE STANDARDS/CODES

The latest editions of the following standards and codes shall be applicable for the materials specified within the scope of this section:

BS 6004/6346			-	PVC insulated cables for lighting & power

BS 6746          		-   	PVC insulation for electrical cables

BS 6360          		-    	Copper conductors

BS 6500          		-    	Insulated flexible cords

4.0	MATERIAL

4.1    	General

The power, lighting and control cables shall be furnished and installed in accordance with the routes and requirements shown on the drawings.

All cables shall have phase identification colours on insulation of each core. The colour code for three phase circuits shall be red, yellow and blue for phase conductors and black for neutral conductor. Where insulated earth conductor is installed, it shall have green or green-yellow colour insulation.

Single-phase circuits shall have insulation of red colour for phase/line, black colour for neutral and green or green-yellow colour for earth conductor.

All DC circuits shall have insulation of white colour for positive, black colour for negative and green or green-yellow colour for earth conductor.

The ends of each length of multi-core armoured or unarmoured cables shall be properly marked for clock-wise and anti clock-wise sequence of core colours.

4.2    	Cables for Conduit or Channel Wiring

All cables/wiring in concealed or surface mounted PVC conduits or in covered channel shall be single core PVC insulated of specified grade and size, unless specifically shown on the drawings or given in BOQ.

4.3    	Cables on surface/concrete trenches

Cables for distribution system to be installed on surface, in cable ducts, in concrete trenches or on trays shall be single or multi-core PVC insulated and PVC sheathed of specified voltage grade and size, unless specifically shown on the drawings or given in BOQ.

  - Cable/Wiring  Inside Lighting Column

All cables/wiring in side lighting column from cable connection box to light fixtures / lanterns shall be 3 core PVC insulated PVC sheathed, high temperature resistant of specified grade and size, unless specifically shown on the drawing or given in the BOQ.

4.5    	Underground Cables

Cables for laying directly underground shall be PVC insulated, PVC sheathed and armoured with galvanized steel/ aluminium wire.  Cables fully installed in underground ducts/pipes and mechanically protected from end to end shall be PVC insulated and PVC sheathed unless specifically shown on the drawings or given in BOQ.

4.6	Cable Markers

Above ground cable markers made of Grade-25 reinforced concrete shall be erected at a maximum interval of 200 metres along the straight trench, at each bend and joint box for indicating the presence of underground cables.  Where the trench changes its direction two number of markers shall be installed one in each direction to indicate the two directions of the trench.  At the joint box, additionally a symbol shall be engraved just beneath the letters MV or LV to indicate the presence of the joint box.  The cable markers shall be finished in grey paint.  The letters and symbols for indication shall be engraved in concrete on both sides.  Letters shall be MV or LV for medium voltage or low voltage cable.  The colour of the engraved letters and symbol shall be red.  The dimensions of the markers shall be as shown on the drawing and shall be installed in the ground as shown.

4.7    	Cable Accessories

All cable accessories shall be provided for the complete cabling and wiring system without any additional cost unless specifically mentioned in BOQ. These shall include but not limited to the items such as saddles, clamps, fixing  channels, connectors, cable joints (where necessary and as approved by the Engineer), clips, lugs, colour sleeves, identification tags, bushes, glands, etc.

5.0	INSTALLATION

5.1    	General

All installation material, labour, tools, cable rollers and accessories for cable installation shall be furnished by the Contractor. The cable and accessories shall be installed as described in accordance with these Specifications, drawings and manufacturer's instructions.

The Contractor shall confirm the exact cut lengths for cable by actual measurements at site prior to the ordering. The cable lengths where shown on the drawings or in BOQ are tentative and only for general guidance. The Contractor shall be solely responsible for furnishing correct lengths of cable to avoid joints in cable length except where necessary, after obtaining approval of the Engineer.

No separate payment for such joints is admissible.

Necessary precautions for safety of cables shall be taken during the laying of cables to avoid scratches/ cuts to the cable surface. Pulling force on cable at all times shall remain well within the manufacturer’s recommended limits.

Prior to installation of jointing and termination kits, the cable lengths shall be checked and tested to ensure that the cables are in sound condition, and no damage has been done during handling and installation.  After  installation, these shall again be tested prior to commissioning as per recommendations of the standards according to which the cable is manufactured.

5.2   	Conduit or Channel Wiring

The wiring through conduit shall be started only after the conduit and channel system is completely installed and all outlet boxes, junction boxes, etc., are fixed in position.

The wires shall be pulled in conduit  or channel with care, preferably without the use of any lubricant. Where necessary and if approved by the Engineer, the cable manufacturer's recommended lubricant may be used. Where several wires are to be installed in the same conduit, they shall be pulled together along with the earth conductor. All wires of same circuit shall be run in one conduit.

The wires shall not be bent to a radius less than ten times the overall diameter of the wire, or more if otherwise recommended by the manufacturer.

The wiring shall be continuous between terminations and looping-in system shall be followed throughout. Any joint in wires shall not be allowed. The use of connectors shall only be allowed at locations where looping-in is rendered difficult. The consent of the Engineer shall be required for using connectors. The connector shall be of suitable rating having porcelain body with  sunk-in screw terminals. The connector shall be wrapped with PVC insulation tape after its installation. A minimum of 150 mm extra length of cable/wire shall be provided at each termination to facilitate repairs in future.

5.3    	Cables on Surface/Trenches

All cables for installation on surface of wall, column, ceiling, trenches, etc., shall be fixed to the surface by means of galvanized steel clips secured to a steel channel using suitable stud plate, nuts and washers.  The distance between each cable clip shall be such so as to support the entire weight of the cable and that distance between the cable & surface and also the vertical clearance between two adjacent cables at any point is 50 mm minimum.  Common mounting channels are to be furnished for cable along the same route.  The Contractor can offer alternate cable fixing arrangement, which shall be approved by the Engineer before commencement of installation.

5.4    	Underground cables

The cables to be installed directly underground shall be laid in trenches in single tiers.  Unless shown specifically on the drawing the depth of cable below finished ground level shall be 900 mm minimum measured from the top of the largest cable to the general ground level.  The burial depth may be increased as required due to site conditions or when crossing other service pipes and roads.  Burial depth less than 900mm and more than 1500mm shall require Engineer's approval.

When cables cross road, paved area, other services or other cables, they shall be laid in protective pipes of required size.  Cables entering the buildings shall also be laid in protective pipes.  The protective pipe ends, after installation of cables, shall be plugged watertight be means of bituminised hesian or equivalent method as approved by the Engineer. A minimum clearance of 250mm vertically and 500mm horizontally shall be maintained between cables and other services.

The cable trench shall be excavated as per route and location shown on the drawings. Before laying of cables in the trench, the bed of the trench shall be leveled and filled with a 100mm thick layer of fine sand (1.3mm diameter maximum particles size). The sand layer shall be leveled and the cables placed thereon. The cables shall be covered with a layer of fine sand 100mm thick measured above the top of the cable. Cable protective bricks shall be placed over the sand cover which shall be of class-C cement concrete, minimum 50mm thick and 300mm square.  The bricks shall be placed over the sand layer and end-to-end to cover the entire length and breadth of the cable trench.  After the concrete bricks are placed, the remainder of the trench shall be backfilled with earth in layer 300mm thick.  Each layer shall be thoroughly tamped and compacted.

A PVC warning tape shall be provided 300 mm below normal ground level covering the entire length and breadth of the trench. The warning tape shall be yellow in colour with marking of danger and voltage of the cable printed in black and as approved by the Engineer.

Cable identification tags of corrosion resistant material shall be tied to cables with PVC cable tie at a maximum of 20 metre interval along the cable length for identification of cable and circuit. The earth continuity conductor shall be laid in the trench with the cables.

Sufficient slack  shall be left in cables  for this purpose the cut lengths of cables shall allow about 3% more in the measured lengths between terminations. At underground joint box, ample slack shall be left to prevent straining of cable joints due to settlement of earth. Payment shall be done as per actual lengths measured at site after installation.

The cut lengths of cables wherever stated are only as a guide. The Contractor shall measure lengths between terminations of each circuit and if the discrepancy between measured lengths at site and the one given on the drawing differ, the Contractor  shall report to Engineer and act  as directed. Cables, whether installed underground or in concrete trenches, shall not be bent to a radius less than 12 times the diameter of the cable or as recommended by the cable manufacturer, whichever is higher.

5.5 	Cable Marker

Above ground, cable markers shall be erected at a 100 metre interval along the straight trench, and at each bend and joint box for indication of presence of underground cable. For more than one metre wide trenches, cable markers shall be provided at both edges of the trench. The cable marker shall bear the necessary instructions indicated in approved colours.

The Contractor shall submit to the Engineer for approval, schedule of cable markers showing location of marker and instructions on each marker.

6.0    	MEASUREMENT AND PAYMENT

6.1    	General

The Contractor's bid amount against each Bill of Quantities item as given  below shall include supply, installation, testing, commissioning and completion for all work specified herein and/or as shown on the Tender Drawing related to the item.

6.2    	Light Circuit Wiring

6.2.1  	Measurement:  Measurement shall be made for the total number of light circuit wiring from LT distribution board to point/switch/push button including wiring between switches/push buttons on the same circuit, acceptably carried out by the Contractor as a complete unit.

6.2.2 	Payment:  Payment shall be made for the total number of units measured, as provided above, at the Contract unit price each and shall constitute full compensation for supplying, installing, connecting, testing, commissioning and completion of the circuit wiring from the LT distribution board to point/switch/push button including wiring between switches/push buttons on the same circuit complete with specified type of surface mounted/concealed conduit, (PVC or steel) required No. specified size single core PVC insulated cable, earth continuity conductor, accessories, etc.

6.3    	Wiring of Light/Fan Point (Point to Switch, Point to Point, Two Way or Group Controlled Light Points)

6.3.1  	Measurement: Measurement shall be made for the total no. of wiring of light/fan points (point to switch, point to point, two way or group controlled light point), acceptably carried out by the Contractor as a complete unit.

6.3.2  	Payment: Payment shall be made for the total number of units measured, as provided above, at the Contract unit price each, and shall constitute full compensation for supplying, installing, connecting, testing, commissioning and completion of the wiring between light point to switch, point to point and  two way light points, including required no. of specified size single core PVC insulated cable, specified type of surface mounted/concealed conduit (PVC or Steel), earth continuity conductor, flexible cable, ceiling rose, one way or two way 10A light control switch, sheet steel box and other accessories, etc.

6.4  	Wiring of Power Circuits (Distributor to load break switch, spur outlets, socket outlets & between sockets)

6.4.1 	Measurement:

6.4.1	Measurement shall be made for the total number of each type of wiring acceptably carried out by the Contractor as a complete unit.

6.4.2  	Payment: Payment shall be made for the total number of units measured, as provided above, at the Contract unit price each and shall constitute full compensation for supplying, installing, connecting, testing, commissioning and completion of wiring of load break switches, spur outlets, socket outlets etc. from LT switchboard / distribution board to load break switches, spur outlets, sockets or between sockets with specified size and number of single core PVC cables including specified type of surface mounted / concealed conduit (PVC or Steel), ECC and all other  accessories etc.

6.5  	LT Cables

6.5.1  	Measurement:  Measurement shall be made for the total running feet for each size and type of LT cable acceptably supplied and installed by the Contractor.

6.5.2	Payment: Payment shall be made for the total running feet of each size and type of LT cable measured, as provided above, at the Contract unit price each and shall constitute full compensation for supplying, installing, connecting, testing and commissioning of the LT cables including all accessories such as cable joints, lugs, colour sleeves, glands, bush, etc. complete with plugging of protective pipe/ sleeve ends for water tightening.

6.6  	Excavation / Backfilling

6.6.1	Measurement:  Measurement shall be made for the total cubic feet of excavation / backfilling of trenches acceptably completed by the contractor according to the specification and as shown on drawings.

6.6.2	Payment: Payment shall be made for the total cubic feet of excavation / backfilling of cable trench measured as carried out above at the contract unit price and shall constitute full completion for excavation / backfilling and all the works related to the item.

No separate payment shall be made for the under mentioned specified work related to the B.O.Q. item excavation and backfilling. The cost thereof shall be deemed to have been included in the quoted rates of above work.

-	Dewatering during excavation and backfilling.

-	Providing and filling of fine sand in trenches.

-	Compacted backfilling of trenches with specified material and disposal of surplus and rejected material.

-	Providing and laying of 300mm x 300mm x 50mm thick concrete (gade-20) protective tiles in trenches.

- Providing and laying of PVC warning tape.

-	Providing above ground cable marker.