SECTION - 8310

TELEPHONE SYSTEM

1.0  	SCOPE OF WORK

The work under this section consists of supplying, installing, testing, commissioning of all material and services of complete telephone system as specified herein, as shown on the Tender Drawings and stated in the Bill of Quantities.

The Contractor shall discuss the electrical layout with the Engineer and co-ordinate at site with other services for exact route, location and position of the system.

The telephone system with accessories shall also comply with the General Specifications, Section 8001 and with other relevant provisions of the Tender Document.

The work shall be undertaken in accordance with applicable rules and regulations of Pak Telecomm Corporation Limited. Any approval/NOC required from PTCL shall be contractors’ responsibility.

2.0  	GENERAL

The system shall comply with the general requirements for telephone system as specified by the Pakistan Telecommunication Authority (PTA). The system shall be capable of accepting analog as well as digital incoming signals. The  system shall be capable of connecting telefax / teletext etc.

3.0	APPLICABLE STANDARDS AND CODE

The latest editions of the following standards/codes shall be applicable for the materials covered within the scope of this section:

DIN    47614		-	Terminal Strips

DIN    40040		-	Class and Reliability of units in Telecommunication

DIN    57800               -	Regulations   for   installation   and    operation   of  	telecommunication.

DIN    57804               -	Telecommunications,   Manufacture   and   Test of 	Apparatus.

CCITT   recommendations  for  ISDN   system and 	Local PTCL/PTA regulations.

ISO 9000-Series

Certified                     -	Manufacturer for quality control

4.0	EQUIPMENT

4.1 	Conduit and Conduit Accessories

The specifications for conduit and conduit accessories shall be same as given in section "Conduits and Pipes" of these specifications.

4.2	Telephone Cable

Cat-5 cable shall be provided for telephone network.

4.3    	Telephone Socket Outlet (RJ45)

The telephone socket outlet back boxes shall have appropriate dimensions made of 16 SWG (1.63mm) sheet steel and suitable arrangement for termination of conduits or of teak wood for installation in dry partitions.

The telephone outlet shall be type RJ45 single/two/three ports as required. The outlet shall be of Clipsal Australia or ‘MK’ UK make or approved equivalent.

4.4    	Distribution Box

Telephone distribution box shall be made of 16 SWG  (1.63mm) sheet steel having required dimensions to accommodate the terminal strips with adequate space available for wiring. The terminal strips shall have provision for tag numbers for telephone extension and with suitable capacity for terminating all incoming and outgoing cables including direct lines. The strip shall be installed on insulated material sheet inside the sheet steel boxes. The termination strip shall provide Insulation Displacement Contact (IDC) technique for easy and quick connection for 0.6 mm. wire size.  The termination strip shall have following minimum specifications:

Insulation Resistance 			> 105 ohm

Dielectric Strength			> 2 kVrms

Termination Resistance 		< 1 ohm

Capacitance between adjacent

Contacts.                        		< 5 pF

Current Carrying Capacity		Disconnection Contact 5 kA 8/20U Sec.

Connection Contact 10 kA 8/20U Sec.

Contacts 				Silver plated brass alloy

Material	Self extinguishing plastic Component according to UL94

The steel box shall be provided with a lockable hinged door. The distribution box shall be suitable for recess mounting.

The distribution box shall be of Krone make or approved equivalent.

5.0 	INSTALLATION

5.1 	Conduit

The telephone conduit shall be installed in accordance with the  instructions and details given in section  "Conduit, and Pipes" of these Specifications.  Telephone and data conduit shall be laid 150mm away from the electrical conduits or cables, and wherever electrical conduits or cables, and telephone and data conduits cross each other, they shall do so at right angles.

Identification marking shall be given at the termination or free end of conduit so that it may not be confused with the electrical conduits. The marking shall be both by colour and by attaching an approved brass tag using brass or bronze tie wire.  Each tag shall be clearly stamped with  "T" for telephone conduit.

5.2  	Telephone Distribution Box

Distribution boxes for telephone cables shall generally be recessed type. The frame of the telephone distribution box shall finish flush with the surface of wall. However, surface type telephone distribution box shall also be acceptable with the approval of the Engineer.

All screws, nuts and bolts used for fixing the box shall be galvanized.  Soft metal bushes shall be used at conduit entries in the box.

5.3    	Telephone Socket Outlet

These shall be installed on the outlet box fixed in the wall, partition and floor.

5.4  	Telephone Cable

The telephone cable shall be installed as outlined in section `L.T. Cables' of these specifications. All cables shall be provided with plastic identification tags at termination, which shall be clearly shown on the As-Built drawings. The complete wiring shall be checked for continuity, identification and insulation before connections are made.

5.5	Training

The Contractor shall provide the services of competent instructors who will give full instruction to the designated personnel in the operation, maintenance of the telephone system.

Training manuals shall be provided for each trainee, which shall describe in detail the information and data imparted in the training programme.

6.0 	MEASUREMENT AND PAYMENT

6.1  	General

The Contractor's bid amount against each Bill of Quantities item as given below shall include supply, installation, testing, commissioning and completion for all works specified herein and/or as shown on the Tender Drawings related to the item.

6.2	Telephone Set

6.2.1	Measurement : Measurement shall be made for the number of each type of telephone sets including 3m extension cable acceptably supplied and installed by the Contractor as a complete unit.

6.2.2	Payment :   Payment  shall be made for the number of units measured as provided above at the contract unit price each and shall constitute full compensation for supplying, installing, testing and commissioning of each type of telephone sets, including 3m extension cable and accessories.

6.3 	Conduits / Pipes

6.3.1 	Measurement: Measurement shall be made for the total running feet of each size of conduits/pipes acceptably supplied and installed by the Contractor.

6.3.2 	Payment: Payment shall be made for the total running feet of conduit measured as provided above at the Contract unit price and shall constitute full compensation for supplying, installing & completion of the laying of the conduits/pipes including jointing materials and accessories, cutting chasing of civil works, excavation and backfilling of ground for under ground PVC conduits, painting, plugging, tagging, etc., as applicable for each type of work.

6.4 	Telephone Cable

6.4.1 	Measurement: Measurement shall be made for each size and type of telephone cable including earth wire as shown on drawing and given in BOQ acceptably supplied and installed by the Contractor between MDF and telephone distribution box as a complete unit.

6.4.2  	Payment: Payment shall be made for the total number of each type of unit measured as provided above at the Contract unit price each and shall constitute full compensation for supplying, installing, testing and commissioning of the required pair of telephone cables including earth wire installed between MDF and telephone distribution box as shown on the drawing and all accessories.

6.5	Telephone Socket Outlet

6.5.1	Measurement: Measurement shall be made of the total number of telephone socket outlet acceptably supplied and installed by the Contractor as a complete unit.

6.5.2  	Payment: Payment shall be made for number of units measured as provided above at the contract unit price each and shall constitute full compensation for supplying, installing, testing, and commissioning of the telephone socket outlet including civil works and all accessories.

6.6 	Telephone Distribution Box

6.6.1	Measurement: Measurement shall be made of the total number of  each type of telephone distribution box as given in BOQ acceptably supplied and installed by the Contractor as a complete job.

6.6.2 	Payment: Payment shall be made for the number of job measured as provided above at the Contract unit price each and shall constitute full compensation for supplying, installing and completion of the telephone distribution box including civil works and all accessories.

6.7 	Wiring of Telephone Outlet/Distribution Boxes

6.7.1	Measurement: Measurement shall be made for the total number of each type of wiring of telephone outlet/distribution boxes,  acceptably carried out by the Contractor  as a complete unit.

6.7.2 	Payment: Payment shall be made for the total number of units measured, as provided above at the contract unit price each, and shall constitute for supplying, installing, connecting, testing, commissioning and completion  of the wiring between telephone  outlet, telephone outlet and distribution box and between distribution boxes  including  required pair of multi-core  telephone  cable  and  appropriate   size conduit and all accessories.