SECTION - 8133

LT DISTRIBUTION BOARDS

1.0 	SCOPE OF WORK

The work under this section consists of supplying, installing, testing, and commissioning of all material and services of the complete Low Tension (LT) Distribution Boards as specified herein, shown on the Tender Drawings and stated in the Bill of Quantities.

The Contractor shall discuss the electrical layout with the Engineer and co-ordinate at site with other services for exact location and position of the each L.T. Distribution Board.

The Low Tension Distribution Board with accessories shall also comply with the General specifications for Electrical Works, section - 8001 and with other relevant provisions of the Tender Document.

2.0 	GENERAL

The Low Tension Distribution Board (DB) shall be sheet steel fabricated suitable for surface/recessed mounting on wall or floor standing totally enclosed, dust tight and vermin proof. It shall be complete in all respect with material and accessories, factory assembled, tested and finished according to the Specifications and to the normal requirements.

The Low Tension Distribution Board shall be front operation type and shall:

- have a rated service short circuit breaking capacity, (Ics), conforming to IEC 60947-2 as shown on the drawings.

- be provided with adequate clearance from live parts so that the flashovers can not be caused by switching, vermin, pests etc.

- be suitable for 415 Volts, 3 phase 4 wire, 50 Hz system.

- be designed  for  flush mounting of all instruments  on  the front side.

- have incoming  and outgoing cable  termination  arrangement, terminal block/line up terminals.

- be provided with stainless steel name plate on the front side of door.

- have all incoming and outgoing connections from top or bottom as per requirement of site conditions.

- have door grounded by flexible copper strip/cable.

- have wiring diagram in the pocket inside the door of Distribution Board

3.0 	APPLICABLE STANDARDS/CODES

The latest editions of the following standards and codes shall be applicable for the materials specified within the scope for this section:

IEC 60051 	- 	Direct setting electrical measuring instruments

IEC 60073 	- 	Colours for indicator lights and push buttons

IEC 60947-2 	- 	Low voltage switchgear and control gear

IEC 60439	- 	Low Voltage Switchgear and Control gear Assemblies.

BS 4752	-	Circuit Breaker

BS 3871	- 	Miniature & Moulded Case Circuit Breakers

BS 88 		- 	HRC fuses

BS 89/90	- 	Ammeters and Voltmeters

BS 3938	- 	Low voltage current transformers

BS 1432	- 	Bus Bars

4.0	MATERIAL

4.1 	Sheet Metal Work

The Low Tension Distribution Board (DB) shall be fabricated with 16 SWG sheet steel recess / surface mounting as approved by the Engineer.  All the components shall be installed on a common component mounting plate inside the enclosure and protected from the front with screwed sheet steel front plate. The enclosure shall be provided with rubber gasketting and a lockable hinged door with cam fastener.

The distribution board shall be supplied complete with all installation materials as recommended by the manufacturer. The incoming and outgoing cable connections shall be according to the wiring requirements. If required, an adapter box for accommodating the cables and conduits may be provided. The box shall be of the same material and finish as the DB. All holes, cutout etc. shall be tool and free from burrs and rough edges.

The cabling inside the DB shall be suitably harnessed by means of straps or cords.  Colour sleeves shall be provided on each cable lugs connected to the bus bars, circuit breakers or terminals for phase identification. An earth bar shall be provided for connection of incoming and outgoing earth conductors.  The earth bar shall be permanently connected to the body of DB at two points. Flexible copper strip shall be provided for earthing of the door of DB.

Circuit numbers/ designation on all circuits shall be conspicuously marked to facilitate connection and maintenance.

All metal work of the DB shall be cleaned down to bare shining metal phosphated and the surfaces chemically prepared for powder coating. Then these shall be coated with powder of colour RAL 7032 and then baked in oven.  The thickness of powder coating shall not be less than 120 microns.

4.2  	Components

The Low Tension Distribution Boards (DB) shall be provided with components as specified, as shown on the Tender Drawings and required for the satisfactory operation of the distribution board and of the electrical system.

Typical component specifications are given below:

4.2.1	Bus Bars

The Bus bars shall be made of 99.9% pure high conductivity electrolytic copper and shall be completely isolated and mechanically braced for the specified fault level. The identification of bus bars shall be by providing colours sleeves on bus bar ends and these shall be red, yellow and blue for phases and black for neutral. The earth bus bar shall be green.

The bus bars shall be for three phase, neutral and earth and shall be of appropriate size to meet the electrical and mechanical requirements of the system. The temperature rise shall not exceed 30oC  at rated current.

4.2.2 	Moulded Case Circuit Breaker (MCCB)

The MCCBs shall be moulded case triple pole 440 Volts or single/double pole 250 Volts of current ratings as shown on the drawings. These shall have fixed magnetic short circuit and adjustable/fixed thermal overload protection.

Under voltage and shunt trip etc. shall also be provided when so required for safe operation and interlock.

The MCCBs shall be installed such that their switching levers are accessible through the front plate for operation.

The single and triple pole MCCBs shall have short circuit rupturing capacity suitable for the distribution system as approved by the Engineer or as shown on the drawings. The MCCBs shall be suitable for working on lighting and power circuits.

4.2.3	Three Phase Energy Meters (Kilowatt Hour Meters)

Three phase energy meters of frequency 50 Hz and accuracy class of 1.0 with proper meter base, cover, frame, terminal block, terminal cover, auxiliary circuit etc. shall be provided for use with instrument transformers. The meter shall be approved by WAPDA/IESCO.

The construction of meter shall be suitable for its purpose in all respect and shall give reasonable assurance of permanence in all mechanical, electrical and magnetic adjustments. The construction shall be such that the meter is not prone to produce appreciable noise in use.

The meter shall have a dust proof case, which can be sealed in such a way that the mechanism of the meter is only accessible after breaking the seal. The case shall be made of metal or toughened glass of a sufficient strength to ensure adequate protection of the internal parts.

The direction of rotation shall be marked by a clearly visible indelible arrow.

Electronic meters with same accuracy class can also be provided subject to no additional cost and approval from WAPDA/IESCO.

Any test(s) to confirm accuracy and confirmation of requirements of specifications and WAPDA/IESCO shall be made. No additional payment shall be admissible for all such tests and is deemed to be included in the cost of the equipment.

4.2.4  	Ammeters and Voltmeters

All meters shall be flush mounting, moving iron, spring controlled. The front dimensions shall be 96 x 96 mm for meters.

The meters shall be of accuracy class 1.5 according to BS-89  and  90.  The  ammeter shall  be  suitable  for connection to 5 Amps secondary of current transformers or directly through shunt as shown on  drawings. The ammeters and voltmeters shall have measuring range  as indicated  on  the  drawings.

4.2.5  	Current Transformers

Air cooled, ring type current transformers shall be provided  having transformation ratio as indicated  on the  drawings.  The  current transformers shall be  of  suitable burden having accuracy class 1.0 according to BS  3938.  The current transformers shall have 5  amps secondary.

4.2.6 	Selector Switches

The ammeter and voltmeter selector switches shall be complete with front plate, grip handle R-Y-B and OFF position for ammeters, and RY-YB-BR-RN-YN-BN and OFF position for voltmeters shall be marked on the respective selector switches.

4.2.7 	Air Break Contactors

The contactors shall be air break, triple pole 415 VAC type  and  suitable for the type of duty (at least utilization Category AC3) to be performed.  The main contacts shall be silver  tipped, butt  type with double break per pole. Each contactor shall be provided with single phase 230 VAC operating coil and minimum one spare normally open and one normally closed auxiliary contact. The number of working auxiliary contacts shall be provided according to the system requirements.

4.2.8 	Push Buttons

The push buttons shall be illuminated, momentary make/break contact type or latch type (push-on/push-off) as required and approved by the Engineer and suitable for flush mounting. The push button for ON and OFF switching shall be red and green respectively. They shall be provided as shown on the drawing.

4.2.9 	Indicating Lamps

Indicating lamps shall be LED type suitable for flush mounting, complete with base. They shall be suitable for operation on 230 V AC and it shall have rosettes of suitable colours as approved by the Engineer. These shall be provided for R, Y, B phases on each distribution board.

4.2.10 	Line up Terminals

Line up terminals wherever provided for control or power circuits shall be suitable for voltage and size of conductors as indicated on drawing.

The line-up terminals for controls shall be suitable for channel mounting.  All necessary accessories such as end plates, fixing clips, transparent label holder caps and label sheets with marking shall be provided.

5.0 	INSTALLATION

The location of low tension distribution boards (DB) are shown diagramatically on the drawings. The actual location shall be determined at site, keeping in view the site conditions and in co-ordination with other equipment, as approved by the Engineer.

Low tension distribution board for recessed mounting in wall shall be installed such that the door shall finish flush with the surface of wall. The recess mounted distribution board shall  be  installed before  the plastering of walls. The DB shall be protected to avoid any damage due to the civil work. Any cuttings, dismantling of the existing wall required for fixing the DB shall be coordinated at site with the approval of Engineer. Any damage done to civil structure shall be made good  by the Contractor.

All loose parts dispatched separately with the DB shall be installed as per manufacturer instructions and all adjustments or setting shall be made as required. All screws, nuts and bolts used for fixing the distribution board shall be galvanized.

The distribution boards installation shall include connecting all incoming and outgoing cables. The cable entry in the boards shall be provided from top or bottom as required and/or as approved by the Engineer.

The distribution boards shall be tested as per instructions contained in article  "Testing" of General Specifications for Electrical Works, Section-8001 of these Specifications.

6.0  	MEASUREMENT AND PAYMENT

6.1 	General

The Contractor's bid amount against each item of Bill of Quantities as given below shall include design, fabrication, supply, installation, testing, commissioning and completion for all works specified herein and/or as shown on the Tender Drawings related to the item.

6.2  	LT Distribution Boards (SMDBs/DBs)

6.2.1 	Measurement: Measurement shall be made for the number of each LT distribution board acceptably supplied and installed by the Contractor as a complete job.

6.2.2 	Payment: Payment shall be made for the number of jobs measured, as provided above, at the Contract unit price each and shall constitute full compensation for design, fabricating, supplying, installing, connecting, testing and commissioning of the LT distribution boards, including fixing arrangement, adapter box and other accessories for complete installation.