SECTION - 8218

HIGH TENSION (H.T.) CABLE TERMINATION KITS

- SCOPE OF WORK

The work under this section consists of supplying of High Tension (HT) cable Termination Kits as specified herein and given in the Bill of Quantities.

2.0	GENERAL

The HT cable termination kits shall be suitable for HT 8.76/15 kV, XLPE copper conductor cables. It shall be suitable for indoor, outdoor and underground installations.

3.0	APPLICABLE STANDARD/CODES

The Latest editions of the relevant standards and codes shall be applicable for the materials within the scope of this Section.

4.0	MATERIAL

4.1	Termination Kits for 8.76/15 kV HT Cables

The termination kits shall be suitable for indoor, outdoor and underground installations. The termination kits shall be complete with all materials.

The HT termination kits shall be from special Silicon skirted or tubular EPDM rubbers.

The tubes shall be pre-stretched to avoid the use of torches or external heat sources.

The HT termination kits shall be supplied complete with stress control tape with a di-electric constant of 30 minimum.

The HT termination kits shall be supplied with all required mounting, installation and operational accessories.

4.2	Straight - Through Joint

The joint-boxes for the cable shall be suitable for indoor or outdoor installation in accordance with the system requirements.

The joint boxes shall be horizontal, straight through, split type. Where installed underground, these shall be suitably protected against corrosion and ingress of moisture. At least two venting holes with plugs shall be provided for compound filling and inspection. Ground straps shall be furnished on the inside of joint box for ground continuity of the cable armor.

4.3	Factory Tests

Physical and electrical acceptance tests in accordance with applicable standard shall be carried out at the manufacturer works. Three copies of test reports will be furnished to the Owner, which shall include brief description of tests, test records and results.

6.0	MEASUREMENT AND PAYMENT

6.1	General

The Contractor's bid amount against each item of Bill of Quantities as given below shall include supply, installation, testing, commissioning and completion for all work specified herein and/or as shown on the Tender Drawing related to the item.

6.2	HT Termination Kit and Straight through Joints

6.2.1	Measurement

Measurement shall be made for each type of HT termination kit/straight through joint acceptably supplied by the manufacturer/supplier as a complete unit.

6.2.2	Payment

Payment be made for the number of units measured, as provided above, at the Contract unit price each and shall constitute full compensation for supply of HT termination kits/straight through joints including all installation accessories, support for joint as required.