SECTION - 8131

HT SWITCHBOARDS

1.0	SCOPE

The work under this section consists of supplying, installing, testing, connecting, commissioning of all material and services of the complete HT switchboards as specified herein or stated on the Tender Drawings and in the Bill of Quantities.

The Contractor shall discuss the electrical layout with the Engineer and co-ordinate at site with other services for exact location and position of the HT Switchboards.

The HT switchboard with accessories shall also comply with the General Specifications for Electrical Works Section-8001 and with other relevant provisions of the Tender Document.

2.0	GENERAL

2.1	H.T. Switchboards

The HT switchboards shall be sheet steel fabricated, floor mounting cubicle type, indoor, totally enclosed, dust tight and vermin proof, and shall have protection class IP-42. It shall be complete in all respect with material and accessories, factory assembled, tested and finished according to the specifications and to the normal requirements.

The switchboard shall be suitable for front operation only and shall:

-    	be suitable for addition of units, on either side, in future.

-    	be provided with adequate clearance from live parts so that flashovers  cannot be caused by switching surges,  vermin,  pests, etc.

-    	be  designed  for  flush mounting of all instruments  on  the  front side.

-    	have all incoming and outgoing connections from the bottom.

-    	have the components mounted so as to facilitate ease of maintenance from the front.

-    	have  provision  for lamp test, alarm test, alarm accept  and  reset facility.

-    	be mounted on cable trenches having their own supporting structure of angular or U steel profiles.

-    	be provided with anti-condensate heater, in each individual enclosure controlled automatically through adjustable humidistat for maintaining required safe operating condition inside the panel and also avoid condensation. The heater shall also be manually operable and provided with protective miniature circuit breaker and ON indication lamp.

-	have stainless steel name plat.

-	have bus bar chamber and instrument chamber.

-	have pocket for wiring diagram in suitable location / door of instruments chamber.

All pertinent details and drawings shall be provided to the Engineer for approval prior to manufacturing. The HT Switchboard shall be manufactured in conformity with the requirements of power supply utility company such as KESC, WAPDA, IESCO, etc, so that approval of power supply connection can be obtained.

3.0	APPLICABLE STANDARDS/CODES

The latest editions of the following standards and codes shall be applicable for the materials within the scope of this section:

IEC 62271-100	High voltage AC circuit breakers

IEC 62271-102	High voltage AC disconnectors and earthing switches

IEC 62271-103	High voltage switches for rated voltage above 1 kV and less than 52 kV

IEC 62271-200	Metal enclosed switchgear and controlgear for rated voltage up to and including 38 kV

IEC 60694	-	Common specifications for high voltage switchgear and controlgear standards

IEC 60044-1	-	Instrument transformers – Current transformers

IEC 60044-2	-	Instrument transformers – Inductive voltage transformers

IEC 60051-1,	-	Direct acting indicating analogue electrical measuring

2, 3, 5 & 8		instruments and their accessories.

IEC 60099-4	-	Surge arresters: Metal oxide surge arresters without gaps for ac system

4.0	MATERIAL

4.1	HT Switchboards

The switchboards shall be fabricated with angle-iron framework, welded, grinded, finished  and  cladded  with  12 SWG  sheet  steel. It shall be suitably  divided  into panels and compartments  for  accommodating  the required number of circuit components, instruments and accessories.

Each cubicle shall be divided in four (04) compartments:

-	breaker compartment

-	busbar compartment

-	H.T. cable connection compartment

-	low voltage compartment to accommodate instruments

All instruments, relays, control and selector switches, indicating lamp, push buttons and trip levers shall be flush mounted and located at convenient heights on the front doors of switchgear in logical and clear manner. Means shall be provided to limit the opening angle of doors to about 100o.

The switchboard shall be supplied complete with foundation bolts and   other installation materials as recommended by the manufacturer. Proper size cable clamping channels shall be provided for fixing  required  size  of 15 kV  XLPE cable. Adequate number of eye bolts shall be provided to facilitate handling.

An earth bar of appropriate cross section  to safely carry the fault current shall be provided on full length of H.T switchboard and connected  to  the body of all sections of the switchboard. The external earth  terminal  shall be provided for main earth connection. The doors shall be grounded by flexible strap of copper braids.

The  control  cabling inside the switchboard shall  be  suitably  numbered and harnessed by means of straps or cords.  All indicating, selecting  and control  equipment  shall  be suitably arranged and  clearly  labelled with flameproof material using indelible ink/marking, indicating the rating and designation of  fuses,  switches etc. The  nameplates shall be provided on the front of  panel  for  each circuit and component, which is accessible from outside. The nameplates shall be of stainless steel with engraved  equipment  designation having minimum width of 5mm. Other labeling on the  switchboard such as danger signs, voltages, switchboard/panel  identification  shall  be  of sufficient size to be legible from a distance of 5 metres.

All metal work of the switchboard shall be cleaned down  to bare shining metal  phosphated  and  the  surfaces  chemically  prepared  for   powder coating. Then these shall be coated with powder of colour RAL 7032 and then   baked in oven. The  thickness of powder coating shall not  be  less than 120 microns.

4.1.1 	Capacity and Basic Data

The switchboard shall be designed to conform to the following requirements:

Rated Current            		: 	As shown on drawings.

Rated Nominal Voltage    	:      	11 kV

Rated Maximum Voltage    	:      	12 kV

Rated Power Frequency     	:      	36 kV for 1 minute

Withstand Voltage (r.m.s.)

Rated Short Circuit      	:      	500 MVA at 11 kV for

Capacity                        		one second.

Rated Symmetrical Breaking	:	25 kA

Current (1 second rating)

Rated Peak withstand 	:      	2.55 times rated

Current				symmetrical breaking

current.

Operating Duty           	:      	B-0.3”-MB-3' -MB

Rated Basic Impulse Level (BIL)   	95 kV

Control Voltage :

a)  Indication/Metering    	:      	110  volt  a.c.  from

secondary of P.T.

b)  Tripping :	Series tripping or 110 volt

D.C. from capacitor trip unit

Heaters and audible 		:	220 V AC from substation LT

alarm        		    		switchboard.

Auxiliary Contacts		:	Provision  for  remote indication  								and/or  as required.

4.1.2	Interlocking

Any interlocking if required inside the HT switchboard and between HT switchboard and  other  equipment  shall be provided  as  stated  on  the drawings.

4.2	Bus Bars

The bus bars shall be made of high conductivity electrolytic tinned copper conductors, suitably protected against corrosion, and shall be completely insulated by heat shrink coloured sleeves of specified voltage and mechanically braced to safely withstand the stresses due to short-time momentary current under the fault conditions. The phase identification of bus bars shall be red, yellow and blue. The clearances shall not be reduced on account of the bus bar insulation or the phase barriers.

4.3 	Circuit Breakers

The circuit breakers shall be triple  pole, withdrawable type, with arc interruption in vacuum. The operating characteristics and technical data shall be as given in art. 4.1.1 of this section.  The bidder shall submit with his offer  the type and details of equipment proposed.

The circuit breakers shall have trip free, direct acting and manually operated drive mechanism. For manual operation a handle shall be provided.  The units shall have rollout trucks and channels for horizontal withdrawal. Interlocking device shall be provided such that the breakers can be closed only when it is in fully plugged-in or fully withdrawn position, and withdrawal of circuit breakers is only possible in the open or isolated position. Safety shutters shall be provided which will automatically cover the live contact as the circuit breaker is withdrawn.    Other interlocks as essentially required for safe and proper operation  of circuit breaker shall be provided. The circuit breaker phases shall be  separated by barriers of approved heat resisting, non-tracking insulating material.

Each circuit breaker shall have a device to register the number of closing operation.

A triple pole grounding switch shall be provided for cable and bus bars earthing, complete  with  mechanism  for interlocking it with the circuit  breaker  and  the roll-out  truck,  and  mechanical  indication to show  the  position  of  grounding switch. The grounding switch shall be rated to safely carry the fault current  due to  inadvertent closing of supply circuit breaker and also for making duty on  the fault.

The  circuit  breakers  shall  have automatic,  mechanically  operated  `ON'  and `OFF'  position indications. The circuit breakers shall be provided with ON-OFF push buttons.

Luminous indications shall be provided on all incoming and outgoing panels, which shall include but not limited to following:

-	Circuit Breaker	ON

-	Circuit Breaker	OFF

-	Circuit Breaker	TRIPPED

-	Heater			ON

Outgoing panel shall additionally be provided with following luminous indications:

-	Buchholz Alarm

-	Buchholz Trip

-	Temperature Alarm

-	Temperature Trip

Each circuit breaker shall be provided with at least three normally closed and three normally open potential free auxiliary contacts rated for 10 Amp, 230V AC as spares. Provision shall be made for remote indication  of the circuit breakers position/status.

A  test  position  shall also be provided to facilitate testing  operation  of  circuit breakers  manually  and  by  protective  relays. Test  socket  with  plug  shall  be provided for testing the relays.

The circuit breakers shall be complete with necessary secondary wiring with ferrules to indicate the circuit. Protection shall also be provided for  all  control circuits.

4.4 	Current Transformers

Each circuit breaker shall be provided with current transformers (CT) having following ratings and characteristics:

-  	Type        		:    	Cast resin

-  	Number      		:    	Three single phase units

-  	Burden       		:    	Suitable for load of protection and 						instrumentation  circuits.

-  	Accuracy     		:    	5P 20 for protection and  1.0   for 								measuring with security  factor 5.

-  	Duty        		:    	For operating relays/meters and  								instruments.

-  	CT ratio      		:    	As shown on the Tender  Drawings.

-  	No. of cores   		:    	1  or  2  as  required  and  as  shown   							on Tender drawings.

-  	Rating and Insulation 	:    	As shown on drawings and/or  				requirement			specification in Article 4.1.1

-  	Rated dynamic	:    	2.55 times rated symmetrical short 				current				circuit current.

4.5	Potential Transformers

Potential  transformers  (PT) shall be provided as shown  on  the  Tender Drawings and having the following ratings and characteristics:

-  	Type        		:    	Cast resin

-  	Number      		:    	Three single phase units.

-  	Burden       		:    	Suitable for load of protection and

instrumentation circuits.

-  	Accuracy     		:    	Class 1.0

-  	Duty        		:    	For operating relays/meters and 								instruments.

PTs shall be designed to have either two independent secondary  windings of specified ratio for connection in star or open delta or with a single secondary windings as required and as shown on single line diagram.

-  	Voltage ratio   		:	11 kV  / 110V / 110V   for double secondary

sqrt 3     sqrt 3    sqrt 3  winding

:	11 kV  / 110V for single secondary winding

sqrt 3    sqrt 3

-  	Rated voltage 		:    	1.2 continuous and 1.5 for 30 seconds.

factor

-  	Rating & insulation	:    	As shown on drawings and/or  				requirements			specification in Article 4.1.1

4.6	Protective relays

The circuit breakers shall be provided with inverse definite minimum time directional or non-directional over-current relays for phase and earth fault protection as shown on drawings. The relays shall have the following common characteristics, unless otherwise specifically mentioned:

-  	Phase fault over

current setting range

Inverse       		:    	50-200% of CT secondary rating

Instantaneous  	:    	200-800% of CT secondary rating.   								The instantaneous elements shall 								also have infinity  setting to  block 								their operation,  if  necessary.

-  	Ground-fault   		:    	20-80% of CT secondary rating   								with instantaneous element as for 								phase fault unit.

-  	Time setting range	:	0-1 second

-  	Connection    		:    	5 Amp secondary  of CT

Tripping		:	110 Volts DC from capacitor trip

unit in each breaker panel or series

tripping.

# -	Indications/Control	:	110 V AC from secondary of P.T.

The relays shall preferably be triple pole type and have positive action without chatter.

4.7	Capacitor Shunt Trip Unit

In case series tripping is not provided, then each circuit breaker in the H.T. switchboard shall be provided with 110 volts direct current trip coils, which will be supplied power through the capacitor trip units. The trip coils shall be fed through the relay contacts and the ‘OFF’ push buttons.

The capacitor trip unit will be fed from 110 volts secondary of potential transformer. The capacitor trip unit shall be suitable for performing two successive tripping operations carried out within five minutes. Every circuit breaker shall be provided with a separate capacitor trip unit.

4.8	Meters & Selector Switches

The meters to be provided on HT switchboard are shown on drawings  and shall be as specified below:

4.8.1 	Ammeter and Voltmeter

The ammeter and voltmeter shall be moving iron spring controlled having front dimensions of 96 x 96 mm. Voltmeters shall have measuring range of 0-15 kV and ammeters measuring range shall be as shown on the drawings. Ammeters and voltmeters shall  conform  to B.S.S. accuracy class 1.5 and suitable for connection to the secondary of PTs and CTs installed on the switchboard.

4.8.2	Selector Switches

Ammeter selector switch shall be R-Y-B-OFF and voltmeter  selector switch  RY-YB-BR-OFF. The selector switches shall be  complete  with front plate and operating lever.

4.8.3 	kWh and kVArh Meters

Kilowatt-hour (kWh) and reactive Kilovolt ampere-hour (kVArh) meters shall be suitable for 3 phase, 3 wire, 50 cycles balanced and unbalanced loads. The kWh meter shall also be provided with maximum demand indicator and built in switch for operation at an interval of 30 minutes.

4.8.4	Alarm Indication

On occurrence of any fault in the system and subsequent tripping of circuit breakers, audio alarm shall be provided on the HT   Switchboard. Push buttons shall be provided on HT Panel for independent resetting of the audio alarm and fault-indicating lamp.  At least  two potential  free contacts rated 10 Amp AC or DC shall  be available for remote connection.

4.9	Surge Protection

Surge Arresters shall be provided in HT switchboard, wherever required, as shown on drawings. The 11 kV surge arresters shall have the following characteristics:

-	Voltage Class (highest system voltage)	:	12 kV rms

-	Service (rated voltage)			:	11 / 1.732 kV rms

-	Peak Current Surge				:	65 kA

This equipment will be tested in accordance with the relevant IEC Standards.

4.10 	Tools

One complete set of tools for routine operation, setting and  maintenance of  HT  switchboard  including  protective  relays  as  recommended by manufacturer of each component shall be  furnished  within  the  price quoted for the HT Switchboard.

HT switchboard shall be provided with independent set of tools placed  in suitable box.  Details of tools shall be furnished by the  bidder with his offer in the relevant schedule of the form of  tender volume - I.

4.11	Insulation Mat

Insulation mat shall be placed in front of the HT panels all along the length. They shall be one meter wide and 6 mm thick and suitable for providing insulation for 15 kV working.

4.12	Danger Boards with Signs & Designation and Shock / First Aid          Charts

As per requirements of Pakistan Electricity Rules/Electric Inspector, Danger Boards having signs and designation of the room shall be installed on the external door of each room of the Substation.

Shock/First Aid Charts shall be installed in HT, LT, Generators and Transformers Rooms.

5.0	INSTALLATION

The HT switchboard shall be installed at location shown on the drawing. The  cable trenches shall be constructed as part of civil works. The Contractor shall  co-ordinate with the civil works for providing any openings, holes, etc., in time to avoid any breakage/damage to completed works. In case such provisions in civil works for installation  of electrical  equipment are not made or made incorrect, the same  shall  be rectified  by  the electrical Contractor at  his  own cost  and to the satisfaction and approval of Engineer.

The Contractor shall provide foundation bolts and grout them in cement concrete floor using non-shrinkable material approved by the Engineer. All installation materials for physically erecting the switchboard, such as bolts, nuts, washers, supporting steel, etc. shall be provided and installed by the Contractor. The switchboard shall be installed upright and in level and shall be firmly and rigidly bolted on the floor and concrete supports. All wiring external from HT Switchboard to alarm indication control unit protection interlock circuits and for auxiliary  power supply for  heaters, etc.,  will  be furnished and installed by the  Contractor  in  consultation with the Engineer.

The switchboard shall be erected as per manufacturer's instructions  and as   approved by the Engineer. Loose parts dispatched by the manufacturer shall be installed and connected as per assembly drawing provided by the manufacturer. Any safety locking of meters, relays, etc., provided  by  the manufacturer for safe transport shall  be  released  only after the switchboard is erected in position.

Necessary provision shall be made in the HT switchboard for incoming/outgoing cables, and installation of cable termination kits, keeping in view both cable and switchboard manufacturer's recommendations. The cable armour shall be connected to the earth system.

The switchboard body shall be connected to earth as per instructions given in section "Earthing" of these Specifications. The switchboard shall be tested and commissioned in the presence of the Engineer. The tests to be carried out shall be as recommended by the International standard to which the switchboard is   manufactured and/or as recommended by manufacturer; but as a minimum the tests given in article  "Testing" of General Specifications for Electrical Works, section 8001 of these Specifications shall be carried out.

6.0	MEASUREMENT AND PAYMENT

6.1 	General

The Contractor's bid amount against each Bill of Quantities item as given below shall include design, supply, installation, testing, commissioning  and completion for all work specified herein and/or as shown on the Tender Drawing related to the item.

6.2       HT Switchboards

6.2.1 	Measurement

Measurement shall be made for the complete job of HT Switchboard acceptably supplied and installed by the Contractor, as a complete job.

6.2.2	Payment

Payment shall be made for the number of jobs measured as provided above at the Contract unit price each and shall constitute full compensation for supplying, installing, connecting, testing, commissioning and completion of the HT switchboard including all connections, installation materials, such as foundation bolts, supporting steel, nuts, washers etc. wiring for control and    auxiliary circuits, tools, etc.

6.3 	HT Insulation Mat

6.3.1	Measurement

Measurement  shall  be  made  for the complete job of Insulating Mat acceptably supplied and installed by the Contractor.

6.3.2	Payment

Payment shall be made for the number of job measured as provided above at the Contract unit price and shall constitute full compensation for supplying and installing and proper placing of insulation mat.

6.4 	Danger Boards with Signs & Designations

and Shock / First Aid Charts

6.4.1	Measurement

Measurement shall be made for complete job of Danger  Board with Signs & Designation and Shock / First Aid Charts acceptably supplied and installed  by  the Contractor as a complete job in accordance with the provisions of Pakistan Electricity Rules and  requirements  of  Electric Inspector.

6.4.2	Payment

Payment shall be made for the number of jobs measured as  provided above at the Contract unit price each and shall constitute   full compensation for supplying and  installing  the  danger boards with signs and designation and shock/first aid charts including all accessories screws, nuts, bolts, etc.